## A
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS --> | 1
BACNET OBJECT FLOOR --> | 0
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 | 41002 | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | 41003 | [8 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 | 41004 | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 | 41005 | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 | 41006 | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | 41007 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | 41008 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | 41009 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | 41010 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | 41011 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | 41012 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | 41013 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | 41014 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | 41015 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | 41016 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | 41017 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | 41018 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | 41019 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | 41020 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | 41021 | [8 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 | 41022 | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | 41023 | [8 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | 41024 | [8 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | 41025 | [8 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | 41026 | [8 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | 41027 | [8 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | 41028 | [8 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | 41029 | [8 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | 41030 | [8 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | 41031 | [8 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | 41032 | [8 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | 41033 | [8 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | 41034 | [8 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | 41035 | [8 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | 41036 | [8 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | 41037 | [8 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 | 41038 | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | 41039 | [8 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | 41040 | [8 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | 41041 | [8 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | 41042 | [8 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | 41043 | [8 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | 41044 | [8 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | 41045 | [8 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 | 41046 | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | 41047 | [8 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | 41048 | [8 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | 41049 | [8 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | 41050 | [8 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | 41051 | [8 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | 41052 | [8 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | 41053 | [8 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 | 41054 | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | 41055 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | 41056 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | 41057 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | 41058 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | 41059 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | 41060 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | 41061 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | 41062 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | 41063 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | 41064 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | 41065 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | 41066 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | 41067 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | 41068 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | 41069 | [8 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 | 41070 | Modbus Device Address |  |  | unit16 | R/W | 1069 | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | 41071 | [8 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 | 41072 | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 | 41073 | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 | 41074 | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | 41075 | [8 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | 41076 | [8 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | 41077 | [8 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 | 41078 | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 | 41079 | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 | 41080 | IP Address |  |  | string(8) | R/W | 1079 | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | 41081 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | 41082 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | 41083 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | 41084 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | 41085 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | 41086 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | 41087 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 | 41088 | Netmask |  |  | string(8) | R/W | 1087 | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | 41089 | [8 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | 41090 | [8 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | 41091 | [8 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | 41092 | [8 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | 41093 | [8 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | 41094 | [8 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | 41095 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 | 41096 | Gateway |  |  | string(8) | R/W | 1095 | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | 41097 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | 41098 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | 41099 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | 41100 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | 41101 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | 41102 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | 41103 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 | 41104 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | 41105 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | 41106 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | 41107 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | 41108 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | 41109 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | 41110 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | 41111 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 | 41112 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | 41113 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | 41114 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | 41115 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | 41116 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | 41117 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | 41118 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | 41119 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 | 41120 | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | 41121 | [8 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | 41122 | [8 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | 41123 | [8 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 | 41124 | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | 41125 | [9 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 | 41126 | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 | 41127 | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 | 41128 | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | 41129 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | 41130 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | 41131 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 | 41132 | Interface baud rate in bits per second |  |  | uint32 | R/W | 1131 | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | 41133 | [8 empty] | system |  |  | ALL
SERIAL BITS | 1133 | 41134 | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 | 41135 | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 | 41136 | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 | 41137 | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 | 41138 | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 | 41139 | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 | 41140 | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 | 41141 | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 | 41142 | Current Avg Element | A | Metrology | float32 | R | 1141 | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | 41143 | [8 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 | 41144 | Current CH1 (A) | A | Metrology | float32 | R | 1143 | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | 41145 | [8 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 | 41146 | Current CH2 (B) | A | Metrology | float32 | R | 1145 | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | 41147 | [8 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 | 41148 | Current CH3 (C) | A | Metrology | float32 | R | 1147 | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | 41149 | [8 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 | 41150 | Voltage L to N Avg Element | V | Metrology | float32 | R | 1149 | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | 41151 | [8 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 | 41152 | Voltage L1 to N (AN) | V | Metrology | float32 | R | 1151 | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | 41153 | [8 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 | 41154 | Voltage L2 to N (BN) | V | Metrology | float32 | R | 1153 | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | 41155 | [8 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 | 41156 | Voltage L3 to N (CN) | V | Metrology | float32 | R | 1155 | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | 41157 | [8 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 | 41158 | Voltage L to L Avg Element | V | Metrology | float32 | R | 1157 | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | 41159 | [8 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 | 41160 | Voltage L1 to L2 (AB) | V | Metrology | float32 | R | 1159 | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | 41161 | [8 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 | 41162 | Voltage L2 to L3 (BC) | V | Metrology | float32 | R | 1161 | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | 41163 | [8 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 | 41164 | Voltage L3 to L1 (CA) | V | Metrology | float32 | R | 1163 | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | 41165 | [8 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 | 41166 | Line Frequency | Hz | Metrology | float32 | R | 1165 | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | 41167 | [8 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 | 41168 | Power Sum Element | kW | Metrology | float32 | R | 1167 | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | 41169 | [8 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 | 41170 | Power CH1 (A) | kW | Metrology | float32 | R | 1169 | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | 41171 | [8 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 | 41172 | Power CH2 (B) | kW | Metrology | float32 | R | 1171 | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | 41173 | [8 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 | 41174 | Power CH3 (C) | kW | Metrology | float32 | R | 1173 | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | 41175 | [8 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 | 41176 | VA Sum Element | kVA | Metrology | float32 | R | 1175 | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | 41177 | [8 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 | 41178 | VA CH1 (A) | kVA | Metrology | float32 | R | 1177 | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | 41179 | [8 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 | 41180 | VA CH2 (B) | kVA | Metrology | float32 | R | 1179 | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | 41181 | [8 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 | 41182 | VA CH3 (C) | kVA | Metrology | float32 | R | 1181 | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | 41183 | [8 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 | 41184 | VAR Sum Element | kVAr | Metrology | float32 | R | 1183 | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | 41185 | [8 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 | 41186 | VAR CH1 (A) | kVAr | Metrology | float32 | R | 1185 | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | 41187 | [8 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 | 41188 | VAR CH2 (B) | kVAr | Metrology | float32 | R | 1187 | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | 41189 | [8 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 | 41190 | VAR CH3 (C) | kVAr | Metrology | float32 | R | 1189 | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | 41191 | [8 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 | 41192 | Apparent PF Avg Element | PF | Metrology | float32 | R | 1191 | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | 41193 | [8 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 | 41194 | Apparent PF CH1 (A) | PF | Metrology | float32 | R | 1193 | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | 41195 | [8 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 | 41196 | Apparent PF CH2 (B) | PF | Metrology | float32 | R | 1195 | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | 41197 | [8 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 | 41198 | Apparent PF CH3 ( C) | PF | Metrology | float32 | R | 1197 | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | 41199 | [8 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 | 41200 | Exported Energy Sum Element | kWh | Metrology | float32 | R | 1199 | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | 41201 | [8 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 | 41202 | Exported Energy CH1 (A) | kWh | Metrology | float32 | R | 1201 | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | 41203 | [8 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 | 41204 | Exported Energy CH2 (B) | kWh | Metrology | float32 | R | 1203 | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | 41205 | [8 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 | 41206 | Exported Energy CH3 (C) | kWh | Metrology | float32 | R | 1205 | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | 41207 | [8 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 | 41208 | Imported Energy Sum Element | kWh | Metrology | float32 | R | 1207 | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | 41209 | [8 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 | 41210 | Imported Energy CH1 (A) | kWh | Metrology | float32 | R | 1209 | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | 41211 | [8 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 | 41212 | Imported Energy CH2 (B) | kWh | Metrology | float32 | R | 1211 | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | 41213 | [8 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 | 41214 | Imported Energy CH3 (C) | kWh | Metrology | float32 | R | 1213 | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | 41215 | [8 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 | 41216 | Exported VAh Sum Element | kVAh | Metrology | float32 | R | 1215 | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | 41217 | [8 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 | 41218 | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R | 1217 | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | 41219 | [8 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 | 41220 | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R | 1219 | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | 41221 | [8 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 | 41222 | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R | 1221 | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | 41223 | [8 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 | 41224 | Imported VAh Sum Element | kVAh | Metrology | float32 | R | 1223 | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | 41225 | [8 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 | 41226 | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R | 1225 | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | 41227 | [8 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 | 41228 | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R | 1227 | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | 41229 | [8 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 | 41230 | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R | 1229 | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | 41231 | [8 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 | 41232 | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R | 1231 | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | 41233 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 | 41234 | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R | 1233 | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | 41235 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 | 41236 | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R | 1235 | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | 41237 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 | 41238 | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R | 1237 | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | 41239 | [8 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 | 41240 | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R | 1239 | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | 41241 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 | 41242 | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R | 1241 | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | 41243 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 | 41244 | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R | 1243 | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | 41245 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 | 41246 | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R | 1245 | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | 41247 | [8 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 | 41248 | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R | 1247 | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | 41249 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 | 41250 | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R | 1249 | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | 41251 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 | 41252 | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R | 1251 | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | 41253 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 | 41254 | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R | 1253 | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | 41255 | [8 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 | 41256 | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R | 1255 | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | 41257 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 | 41258 | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R | 1257 | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | 41259 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 | 41260 | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R | 1259 | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | 41261 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 | 41262 | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R | 1261 | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | 41263 | [8 empty] | element |  |  | ALL
Events MSW | 1263 | 41264 | Events MSW |  |  | bitfield32 | R | 1263 | AI | Events | system |  |  | ALL
Events LSW | 1264 | 41265 | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 | 41266 | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 | 41267 | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
FACTORY REGISTERS | - | - | FACTORY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Factory Unlock Register | 2000 | 42001 | Factory Unlock Register |  | Factory | unit16 | R/W |  |  |  | system |  | Reserved | ALL
Factory Reset | 2001 | 42002 | Factory Reset |  | Factory | unit16 | R/W |  |  |  | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
OEM Vendor ID | 2002 | 42003 | OEM Vendor ID |  | Factory | unit16 | R |  |  |  | system |  | Reserved | ALL
FACTORY_CONFIG | 2003 | 42004 | Factory Config |  | Factory | unit16 | R |  |  |  | system | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable | ALL
USER COMMAND POINTS | - | - | USER COMMAND POINTS | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 | 42101 | Reset (software) processor |  | User | unit16 | W | 2100 | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 | 42102 | Clear all accumulated measurements (CAM) |  | User | unit16 | W | 2101 | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 | 42103 | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W | 2102 | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 | 42104 | Clear Peak Demand Element |  | User | unit16 | W | 2103 | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 | 42105 | Clear Peak Demand All |  | User | unit16 | W | 2104 | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 | 42106 | Reset to User Defaults |  | User | unit16 | W | 2105 | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - | USER CONFIG POINTS | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 | 42202 | Sliding or Fixed |  | Config | enum16 | R | 2201 | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 | 42203 | Demand Window | Min | Config | uint16 | R | 2202 | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 | 42204 | Volt Multiplier VINPUT1 |  | Config | float32 | R/W | 2203 | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | 42205 | [8 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 | 42206 | Volt Multiplier VINPUT2 |  | Config | float32 | R/W | 2205 | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | 42207 | [8 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 | 42208 | Service Type |  | Config | enum16 | R/W | 2207 | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 | 42209 | Snap MV Threshold | PER | Config | float32 | R/W | 2208 | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | 42210 | [8 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 | 42211 | Snap Rog Threshold | PER | Config | float32 | R/W | 2210 | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | 42212 | [8 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 | 42213 | Snap Volt Threshold | V | Config | float32 | R/W | 2212 | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | 42214 | [8 empty] | system |  |  | ALL
Communications Mode | 2214 | 42215 | Communications Mode |  | Config |  |  | 2214 | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 | 42216 | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W | 2215 | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | 42217 | [8 empty] | system |  |  | ALL
Voltage Input Element | 2217 | 42218 | Element Voltage Input |  | Config | enum16 | R/W | 2217 | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 | 42219 | CT1 RANGE | A | Config | float32 | R/W | 2218 | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | 42220 | [8 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 | 42221 | Voltage Reference for CT1 |  | Config | enum16 | R/W | 2220 | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 | 42222 | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W | 2221 | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | 42223 | [8 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 | 42224 | CT1 TYPE |  | Config | enum16 | R/W | 2223 | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 | 42225 | CT1 PHASE SHIFT | Deg | Config | float32 | R/W | 2224 | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | 42226 | [8 empty] | element |  |  | ALL
CH1 CT Sign | 2226 | 42227 | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W | 2226 | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 | 42228 | CT2 RANGE | A | Config | float32 | R/W | 2227 | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | 42229 | [8 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 | 42230 | Voltage Reference for CT2 |  | Config | enum16 | R/W | 2229 | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 | 42231 | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W | 2230 | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | 42232 | [8 empty] | element | >0 |  | ALL
CH2 CT type | 2232 | 42233 | CT2 TYPE |  | Config | enum16 | R/W | 2232 | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 | 42234 | CT2 PHASE SHIFT | Deg | Config | float32 | R/W | 2233 | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | 42235 | [8 empty] | element |  |  | ALL
CH2 CT Sign | 2235 | 42236 | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W | 2235 | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 | 42237 | CT3 INTEGER | A | Config | float32 | R/W | 2236 | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | 42238 | [8 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 | 42239 | Voltage Reference for CT3 |  | Config | enum16 | R/W | 2238 | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 | 42240 | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W | 2239 | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | 42241 | [8 empty] | element | >0 |  | ALL
CH3 CT type | 2241 | 42242 | CT3 TYPE |  | Config | enum16 | R/W | 2241 | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 | 42243 | CT3 PHASE SHIFT | Deg | Config | float32 | R/W | 2242 | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | 42244 | [8 empty] | element |  |  | ALL
CH3 CT Sign | 2244 | 42245 | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W | 2244 | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 | 42246 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 | 42247 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 | 42248 | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 | 42249 | PF Sign Convention |  | Config | uint16 | R/W | 2248 | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 | 42250 | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 | 42251 | BACnet UDP Port |  | Config | uint16 | R/W | 2250 | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 | 42252 | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 | 42253 | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | 42254 | [8 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 | 42261 | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | 42262 | [11 empty] | ALL
BACnet Max Info Frames | 2262 | 42263 | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 | 42264 | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 | 42265 | BBMD IP Address |  | Config | string(16) | R/W | 2264 | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | 42266 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | 42267 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | 42268 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | 42269 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | 42270 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | 42271 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | 42272 | [9 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 | 42273 | LCD/WebApp Read Password |  | Config | uint16 | R/W | 2272 | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 | 42274 | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 | 42275 | Customer Line frequency |  | Config | float | R/W | 2274 | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | 42276 | [10 empty] | Reserved | ALL
Communications Interface Configured | 2276 | 42277 | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 | 42278 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 | 42279 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 | 42280 | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 | 42281 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 | 42282 | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 | 42283 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 | 42284 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 | 42285 | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 | 42286 | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 | 42287 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 | 42288 | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 | 42289 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 | 42290 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 | 42291 | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 | 42292 | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | 42293 | [11 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 | 42294 | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | 42295 | [11 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 | 42296 | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 | 42297 | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - | METROLOGY POINTS | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 | 42301 | Displacement PF Avg Element | dPF | Metrology | float32 | R | 2300 | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | 42302 | [11 empty] | ALL
Displacement PF CH1 (MSW) | 2302 | 42303 | Displacement PF CH1 (A) | dPF | Metrology | float32 | R | 2302 | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | 42304 | [11 empty] | ALL
Displacement PF CH2 (MSW) | 2304 | 42305 | Displacement PF CH2 (B) | dPF | Metrology | float32 | R | 2304 | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | 42306 | [11 empty] | ALL
Displacement PF CH3 (MSW) | 2306 | 42307 | Displacement PF CH3 (C) | dPF | Metrology | float32 | R | 2306 | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | 42308 | [11 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 | 42309 | Avg Apparent PF Element | aPF | Metrology | float32 | R | 2308 | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | 42310 | [11 empty] | ALL
Apparent PF CH1 (MSW) | 2310 | 42311 | Apparent PF CH1 (A) | aPF | Metrology | float32 | R | 2310 | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | 42312 | [11 empty] | ALL
Apparent PF CH2 (MSW) | 2312 | 42313 | Apparent PF CH2 (B) | aPF | Metrology | float32 | R | 2312 | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | 42314 | [11 empty] | ALL
Apparent PF CH3 (MSW) | 2314 | 42315 | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R | 2314 | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | 42316 | [11 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 | 42317 | Distortion PF Avg Element | tPF | Metrology | float32 | R | 2316 | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | 42318 | [11 empty] | ALL
Distortion PF CH1 (MSW) | 2318 | 42319 | Distortion PF CH1 (A) | tPF | Metrology | float32 | R | 2318 | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | 42320 | [11 empty] | ALL
Distortion PF CH2 (MSW) | 2320 | 42321 | Distortion PF CH2 (B) | tPF | Metrology | float32 | R | 2320 | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | 42322 | [11 empty] | ALL
Distortion PF CH3 (MSW) | 2322 | 42323 | Distortion PF CH3 (C) | tPF | Metrology | float32 | R | 2322 | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | 42324 | [11 empty] | ALL
THD Avg Element (MSW) | 2324 | 42325 | THD Avg Element | % | Metrology | float32 | R | 2324 | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | 42326 | [11 empty] | ALL
THD CH1 (MSW) | 2326 | 42327 | THD CH1 (A) | % | Metrology | float32 | R | 2326 | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | 42328 | [11 empty] | ALL
THD CH2 (MSW) | 2328 | 42329 | THD CH2 (B) | % | Metrology | float32 | R | 2328 | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | 42330 | [11 empty] | ALL
THD CH3 (MSW) | 2330 | 42331 | THD CH3 (C) | % | Metrology | float32 | R | 2330 | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | 42332 | [11 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 | 42333 | Power Demand Max Interval Element | kW | Metrology | float32 | R | 2332 | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | 42334 | [11 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 | 42335 | Power Demand This Interval Element | kW | Metrology | float32 | R | 2334 | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | 42336 | [11 empty] | ALL
VA Peak Demand Element (MSW) | 2336 | 42337 | VA Demand Max Interval Element | kVA | Metrology | float32 | R | 2336 | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | 42338 | [11 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 | 42339 | VA Demand This Interval Element | kVA | Metrology | float32 | R | 2338 | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | 42340 | [11 empty] | ALL
Not Used | 2340 | 42341 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 | 42342 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 | 42343 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 | 42344 | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 | 42345 | Energy Net Sum Element | kWh | Metrology | float32 | R | 2344 | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | 42346 | [8 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 | 42347 | Energy Net CH1 | kWh | Metrology | float32 | R | 2346 | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | 42348 | [8 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 | 42349 | Energy Net CH2 | kWh | Metrology | float32 | R | 2348 | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | 42350 | [8 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 | 42351 | Energy Net CH3 | kWh | Metrology | float32 | R | 2350 | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | 42352 | [8 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 | 42353 | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R | 2352 | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | 42354 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 | 42355 | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R | 2354 | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | 42356 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 | 42357 | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R | 2356 | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | 42358 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 | 42359 | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R | 2358 | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | 42360 | [8 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 | 42361 | VARh Net Sum Element | kVArh | Metrology | float32 | R | 2360 | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | 42362 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 | 42363 | VARh Net CH1 | kVArh | Metrology | float32 | R | 2362 | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | 42364 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 | 42365 | VARh Net CH2 | kVArh | Metrology | float32 | R | 2364 | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | 42366 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 | 42367 | VARh Net CH3 | kVArh | Metrology | float32 | R | 2366 | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | 42368 | [8 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 | 42369 | Time Since Reset MSW | Sec | Metrology | uint32 |  | 2368 | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 | 42370 | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 | 42371 | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 | 42372 | CH1 Angle | Deg | Metrology | float32 | R | 2371 | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | 42373 | [8 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 | 42374 | CH2 Angle | Deg | Metrology | float32 | R | 2373 | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | 42375 | [8 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 | 42376 | CH3 Angle | Deg | Metrology | float32 | R | 2375 | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | 42377 | [11 empty] | ALL
Phase Chek System Status | 2377 | 42378 | System Phase Check Status |  | Metrology | bitfield16 | R | 2377 | BV | Phase Check System Status | system | 0,1 | 0 (All Channels OK), 1(Somewhere a channel is reading a dPF < 0.55), check register 2378 for each Element | ALL
Phase Chek Element Status | 2378 | 42379 | Element Phase Check Status |  | Metrology | bitfield16 | R | 2378 | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 | 42380 | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 | 42381 | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 | 42382 | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 | 42392 | Element Angle |  | Metrology | float | R | 2391 | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | 42393 | [11 empty] | ALL
PULSE INPUTS | - | - | PULSE INPUTS | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 | 42401 | Pulse Input 1 Enable |  | Config | uint16 | R/W | 2400 | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 | 42402 | Pulse Input 1 Scale Factor |  | Config | float32 | R/W | 2401 | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 | 42403 |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 | 42404 | Pulse Input 1 Units |  | Config | string(4) | R/W | 2403 | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 | 42405 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 | 42406 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 | 42407 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 | 42408 | Pulse Input 1 Accumulator |  | Metrology | float32 | R | 2407 | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | 42409 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 | 42410 | Pulse Input 1 Accumulator Clear |  | User | unit16 | W | 2409 | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 | 42411 | Pulse Input 2 Enable |  | Config | uint16 | R/W | 2410 | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 | 42412 | Pulse Input 2 Scale Factor |  | Config | float32 | R/W | 2411 | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | 42413 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 | 42414 | Pulse Input 2 Units |  | Config | string(4) | R/W | 2413 | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 | 42415 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 | 42416 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 | 42417 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 | 42418 | Pulse Input 2 Accumulator |  | Metrology | float32 | R | 2417 | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | 42419 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 | 42420 | Pulse Input 2 Accumulator Clear |  | User | unit16 | W | 2419 | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 | 42421 | Pulse Input 3 Enable |  | Config | uint16 | R/W | 2420 | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 | 42422 | Pulse Input 3 Scale Factor |  | Config | float32 | R/W | 2421 | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | 42423 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 | 42424 | Pulse Input 3 Units |  | Config | string(4) | R/W | 2423 | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 | 42425 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 | 42426 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 | 42427 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 | 42428 | Pulse Input 3 Accumulator |  | Metrology | float32 | R | 2427 | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | 42429 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 | 42430 | Pulse Input 3 Accumulator Clear |  | User |  | W | 2429 | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 | 42431 | Pulse Input 4 Enable |  | Config | uint16 | R/W | 2430 | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 | 42432 | Pulse Input 4 Scale Factor |  | Config | float32 | R/W | 2431 | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | 42433 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 | 42434 | Pulse Input 4 Units |  | Config | string(4) | R/W | 2433 | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 | 42435 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 | 42436 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 | 42437 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 | 42438 | Pulse Input 4 Accumulator |  | Metrology | float32 | R | 2437 | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | 42439 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 | 42440 | Pulse Input 4 Accumulator Clear |  | User | unit16 | W | 2439 | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - | ALARMS | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 | 42452 | State of Alarm |  | Metrology | uint16 | R/W | 2451 | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 | 42453 | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 | 42454 | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 | 42455 | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 | 42456 | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 | 42457 | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 | 42458 | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 | 42459 | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W | 2458 | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 | 42460 | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W | 2459 | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Range Vin1 L1N Under | 2460 | 42461 | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W | 2460 | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 | 42462 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2N Under | 2462 | 42463 | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W | 2462 | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 | 42464 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3N Under | 2464 | 42465 | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W | 2464 | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 | 42466 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L1L2 Under | 2466 | 42467 | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W | 2466 | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 | 42468 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2L3 Under | 2468 | 42469 | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W | 2468 | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 | 42470 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3L1 Under | 2470 | 42471 | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W | 2470 | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 | 42472 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin2 L1N Under | 2472 | 42473 | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W | 2472 | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 | 42474 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2N Under | 2474 | 42475 | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W | 2474 | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 | 42476 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3N Under | 2476 | 42477 | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W | 2476 | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 | 42478 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L1L2 Under | 2478 | 42479 | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W | 2478 | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 | 42480 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2L3 Under | 2480 | 42481 | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W | 2480 | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 | 42482 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3L1 Under | 2482 | 42483 | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W | 2482 | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 | 42484 | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 | 42485 | Voltage Alarm Persistence | Sec | Config | uint16 | R/W | 2484 | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 | 42486 | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R | 2485 | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 | 42487 | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 | 42488 | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R | 2487 | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 | 42489 | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 | 42490 | Real Time Clock MSW |  | Config | uint16 | R/W | 2489 | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 | 42491 | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - | USER CONFIG POINTS 2 | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 | 42602 | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 | 42603 | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 | 42604 | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 | 42605 | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 | 42606 | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 | 42607 | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 | 42608 | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 | 42609 | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 | 42610 | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 | 42611 | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 | 42612 | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 | 42613 | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 | 42614 | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 | 42615 | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 | 42616 | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 | 42617 | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 | 42618 | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 | 42619 | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 | 42620 | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 | 42621 | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 | 42622 | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 | 42623 | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 | 42624 | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 | 42625 | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 | 42626 | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 | 42627 | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 | 42628 | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 | 42629 | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 | 42630 | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 | 42631 | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 | 42632 | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 | 42633 | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 | 42634 | BACnet Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | 2634 | 42635 | BACnet Description 1 | [8 empty] | 2 Char |  | ALL
BACnet Description 2 | 2635 | 42636 | BACnet Description 2 | [8 empty] | 2 Char |  | ALL
BACnet Description 3 | 2636 | 42637 | BACnet Description 3 | [8 empty] | 2 Char |  | ALL
BACnet Description 4 | 2637 | 42638 | BACnet Description 4 | [8 empty] | 2 Char |  | ALL
BACnet Description 5 | 2638 | 42639 | BACnet Description 5 | [8 empty] | 2 Char |  | ALL
BACnet Description 6 | 2639 | 42640 | BACnet Description 6 | [8 empty] | 2 Char |  | ALL
BACnet Description 7 | 2640 | 42641 | BACnet Description 7 | [8 empty] | 2 Char |  | ALL
BACnet Description 8 | 2641 | 42642 | BACnet Description 8 | [8 empty] | 2 Char |  | ALL
BACnet Description 9 | 2642 | 42643 | BACnet Description 9 | [8 empty] | 2 Char |  | ALL
BACnet Description 10 | 2643 | 42644 | BACnet Description 10 | [8 empty] | 2 Char |  | ALL
BACnet Description 11 | 2644 | 42645 | BACnet Description 11 | [8 empty] | 2 Char |  | ALL
BACnet Description 12 | 2645 | 42646 | BACnet Description 12 | [8 empty] | 2 Char |  | ALL
BACnet Description 13 | 2646 | 42647 | BACnet Description 13 | [8 empty] | 2 Char |  | ALL
BACnet Description 14 | 2647 | 42648 | BACnet Description 14 | [8 empty] | 2 Char |  | ALL
BACnet Description 15 | 2648 | 42649 | BACnet Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
VERIS EMULATION LEGACY REGISTERS | - | - | VERIS EMULATION LEGACY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Veris Emulation Mode | 2200 | 42201 | Set to Veris Emulation Mode |  | Config | uint16 | R/W |  |  |  | system | 0-1 | 1 = Report Slave ID as Veris Model H8036 | ALL
kWh System LSW | 0 | 40001 | kWh System LSW | kWh | Veris | uint32 | R |  |  |  | element |  |  | ALL
kWh System MSW | 1 | 40002 | kWh System MSW | kWh | Veris |  | R |  |  |  | element |  |  | ALL
kW System | 2 | 40003 | kW System | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVAR System | 3 | 40004 | kVAR System | kVAR | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVA System | 4 | 40005 | kVA System | kVA | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF System | 5 | 40006 | Apparent PF System | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts Line to Line Avg | 6 | 40007 | Volts Line to Line Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts Line to Neutral Avg | 7 | 40008 | Volts Line to Neutral Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps System Avg | 8 | 40009 | Amps System Avg | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L1 | 9 | 40010 | kW L1 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L2 | 10 | 40011 | kW L2 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L3 | 11 | 40012 | kW L3 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L1 | 12 | 40013 | Apparent PF L1 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L2 | 13 | 40014 | Apparent PF L2 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L3 | 14 | 40015 | Apparent PF L3 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts L1 to L2 | 15 | 40016 | Volts L1 to L2 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to L3 | 16 | 40017 | Volts L2 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to L3 | 17 | 40018 | Volts L1 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to Neutral | 18 | 40019 | Volts L1 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to Neutral | 19 | 40020 | Volts L2 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L3 to Neutral | 20 | 40021 | Volts L3 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps L1 | 21 | 40022 | Amps L1 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L2 | 22 | 40023 | Amps L2 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L3 | 23 | 40024 | Amps L3 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW System Avg | 24 | 40025 | kW System Avg | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Now | 25 | 40026 | kW Demand Sys Now (was Min) | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Max | 26 | 40027 | kW Demand Sys Max | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL

## B
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS --> | 2
BACNET OBJECT FLOOR --> | 10000
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 | 41002 | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | 41003 | [8 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 | 41004 | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 | 41005 | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 | 41006 | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | 41007 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | 41008 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | 41009 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | 41010 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | 41011 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | 41012 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | 41013 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | 41014 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | 41015 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | 41016 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | 41017 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | 41018 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | 41019 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | 41020 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | 41021 | [8 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 | 41022 | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | 41023 | [8 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | 41024 | [8 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | 41025 | [8 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | 41026 | [8 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | 41027 | [8 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | 41028 | [8 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | 41029 | [8 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | 41030 | [8 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | 41031 | [8 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | 41032 | [8 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | 41033 | [8 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | 41034 | [8 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | 41035 | [8 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | 41036 | [8 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | 41037 | [8 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 | 41038 | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | 41039 | [8 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | 41040 | [8 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | 41041 | [8 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | 41042 | [8 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | 41043 | [8 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | 41044 | [8 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | 41045 | [8 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 | 41046 | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | 41047 | [8 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | 41048 | [8 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | 41049 | [8 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | 41050 | [8 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | 41051 | [8 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | 41052 | [8 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | 41053 | [8 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 | 41054 | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | 41055 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | 41056 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | 41057 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | 41058 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | 41059 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | 41060 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | 41061 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | 41062 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | 41063 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | 41064 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | 41065 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | 41066 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | 41067 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | 41068 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | 41069 | [8 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 | 41070 | Modbus Device Address |  |  | unit16 | R/W | 1069 | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | 41071 | [8 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 | 41072 | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 | 41073 | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 | 41074 | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | 41075 | [8 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | 41076 | [8 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | 41077 | [8 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 | 41078 | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 | 41079 | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 | 41080 | IP Address |  |  | string(8) | R/W | 1079 | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | 41081 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | 41082 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | 41083 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | 41084 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | 41085 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | 41086 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | 41087 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 | 41088 | Netmask |  |  | string(8) | R/W | 1087 | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | 41089 | [8 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | 41090 | [8 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | 41091 | [8 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | 41092 | [8 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | 41093 | [8 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | 41094 | [8 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | 41095 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 | 41096 | Gateway |  |  | string(8) | R/W | 1095 | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | 41097 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | 41098 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | 41099 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | 41100 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | 41101 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | 41102 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | 41103 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 | 41104 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | 41105 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | 41106 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | 41107 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | 41108 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | 41109 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | 41110 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | 41111 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 | 41112 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | 41113 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | 41114 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | 41115 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | 41116 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | 41117 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | 41118 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | 41119 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 | 41120 | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | 41121 | [8 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | 41122 | [8 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | 41123 | [8 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 | 41124 | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | 41125 | [9 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 | 41126 | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 | 41127 | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 | 41128 | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | 41129 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | 41130 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | 41131 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 | 41132 | Interface baud rate in bits per second |  |  | uint32 | R/W | 1131 | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | 41133 | [8 empty] | system |  |  | ALL
SERIAL BITS | 1133 | 41134 | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 | 41135 | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 | 41136 | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 | 41137 | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 | 41138 | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 | 41139 | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 | 41140 | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 | 41141 | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 | 41142 | Current Avg Element | A | Metrology | float32 | R | 11141 | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | 41143 | [8 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 | 41144 | Current CH1 (A) | A | Metrology | float32 | R | 11143 | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | 41145 | [8 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 | 41146 | Current CH2 (B) | A | Metrology | float32 | R | 11145 | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | 41147 | [8 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 | 41148 | Current CH3 (C) | A | Metrology | float32 | R | 11147 | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | 41149 | [8 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 | 41150 | Voltage L to N Avg Element | V | Metrology | float32 | R | 11149 | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | 41151 | [8 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 | 41152 | Voltage L1 to N (AN) | V | Metrology | float32 | R | 11151 | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | 41153 | [8 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 | 41154 | Voltage L2 to N (BN) | V | Metrology | float32 | R | 11153 | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | 41155 | [8 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 | 41156 | Voltage L3 to N (CN) | V | Metrology | float32 | R | 11155 | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | 41157 | [8 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 | 41158 | Voltage L to L Avg Element | V | Metrology | float32 | R | 11157 | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | 41159 | [8 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 | 41160 | Voltage L1 to L2 (AB) | V | Metrology | float32 | R | 11159 | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | 41161 | [8 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 | 41162 | Voltage L2 to L3 (BC) | V | Metrology | float32 | R | 11161 | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | 41163 | [8 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 | 41164 | Voltage L3 to L1 (CA) | V | Metrology | float32 | R | 11163 | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | 41165 | [8 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 | 41166 | Line Frequency | Hz | Metrology | float32 | R | 11165 | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | 41167 | [8 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 | 41168 | Power Sum Element | kW | Metrology | float32 | R | 11167 | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | 41169 | [8 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 | 41170 | Power CH1 (A) | kW | Metrology | float32 | R | 11169 | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | 41171 | [8 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 | 41172 | Power CH2 (B) | kW | Metrology | float32 | R | 11171 | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | 41173 | [8 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 | 41174 | Power CH3 (C) | kW | Metrology | float32 | R | 11173 | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | 41175 | [8 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 | 41176 | VA Sum Element | kVA | Metrology | float32 | R | 11175 | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | 41177 | [8 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 | 41178 | VA CH1 (A) | kVA | Metrology | float32 | R | 11177 | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | 41179 | [8 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 | 41180 | VA CH2 (B) | kVA | Metrology | float32 | R | 11179 | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | 41181 | [8 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 | 41182 | VA CH3 (C) | kVA | Metrology | float32 | R | 11181 | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | 41183 | [8 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 | 41184 | VAR Sum Element | kVAr | Metrology | float32 | R | 11183 | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | 41185 | [8 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 | 41186 | VAR CH1 (A) | kVAr | Metrology | float32 | R | 11185 | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | 41187 | [8 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 | 41188 | VAR CH2 (B) | kVAr | Metrology | float32 | R | 11187 | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | 41189 | [8 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 | 41190 | VAR CH3 (C) | kVAr | Metrology | float32 | R | 11189 | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | 41191 | [8 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 | 41192 | Apparent PF Avg Element | PF | Metrology | float32 | R | 11191 | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | 41193 | [8 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 | 41194 | Apparent PF CH1 (A) | PF | Metrology | float32 | R | 11193 | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | 41195 | [8 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 | 41196 | Apparent PF CH2 (B) | PF | Metrology | float32 | R | 11195 | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | 41197 | [8 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 | 41198 | Apparent PF CH3 ( C) | PF | Metrology | float32 | R | 11197 | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | 41199 | [8 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 | 41200 | Exported Energy Sum Element | kWh | Metrology | float32 | R | 11199 | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | 41201 | [8 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 | 41202 | Exported Energy CH1 (A) | kWh | Metrology | float32 | R | 11201 | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | 41203 | [8 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 | 41204 | Exported Energy CH2 (B) | kWh | Metrology | float32 | R | 11203 | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | 41205 | [8 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 | 41206 | Exported Energy CH3 (C) | kWh | Metrology | float32 | R | 11205 | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | 41207 | [8 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 | 41208 | Imported Energy Sum Element | kWh | Metrology | float32 | R | 11207 | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | 41209 | [8 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 | 41210 | Imported Energy CH1 (A) | kWh | Metrology | float32 | R | 11209 | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | 41211 | [8 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 | 41212 | Imported Energy CH2 (B) | kWh | Metrology | float32 | R | 11211 | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | 41213 | [8 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 | 41214 | Imported Energy CH3 (C) | kWh | Metrology | float32 | R | 11213 | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | 41215 | [8 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 | 41216 | Exported VAh Sum Element | kVAh | Metrology | float32 | R | 11215 | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | 41217 | [8 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 | 41218 | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R | 11217 | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | 41219 | [8 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 | 41220 | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R | 11219 | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | 41221 | [8 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 | 41222 | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R | 11221 | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | 41223 | [8 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 | 41224 | Imported VAh Sum Element | kVAh | Metrology | float32 | R | 11223 | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | 41225 | [8 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 | 41226 | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R | 11225 | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | 41227 | [8 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 | 41228 | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R | 11227 | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | 41229 | [8 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 | 41230 | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R | 11229 | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | 41231 | [8 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 | 41232 | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R | 11231 | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | 41233 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 | 41234 | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R | 11233 | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | 41235 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 | 41236 | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R | 11235 | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | 41237 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 | 41238 | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R | 11237 | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | 41239 | [8 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 | 41240 | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R | 11239 | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | 41241 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 | 41242 | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R | 11241 | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | 41243 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 | 41244 | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R | 11243 | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | 41245 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 | 41246 | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R | 11245 | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | 41247 | [8 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 | 41248 | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R | 11247 | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | 41249 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 | 41250 | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R | 11249 | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | 41251 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 | 41252 | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R | 11251 | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | 41253 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 | 41254 | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R | 11253 | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | 41255 | [8 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 | 41256 | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R | 11255 | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | 41257 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 | 41258 | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R | 11257 | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | 41259 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 | 41260 | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R | 11259 | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | 41261 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 | 41262 | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R | 11261 | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | 41263 | [8 empty] | element |  |  | ALL
Events MSW | 1263 | 41264 | Events MSW |  |  | bitfield32 | R | 1263 | AI | Events | system |  |  | ALL
Events LSW | 1264 | 41265 | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 | 41266 | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 | 41267 | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
FACTORY REGISTERS | - | - | FACTORY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Factory Unlock Register | 2000 | 42001 | Factory Unlock Register |  | Factory | unit16 | R/W |  |  |  | system |  | Reserved | ALL
Factory Reset | 2001 | 42002 | Factory Reset |  | Factory | unit16 | R/W |  |  |  | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
OEM Vendor ID | 2002 | 42003 | OEM Vendor ID |  | Factory | unit16 | R |  |  |  | system |  | Reserved | ALL
FACTORY_CONFIG | 2003 | 42004 | Factory Config |  | Factory | unit16 | R |  |  |  | system | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable | ALL
USER COMMAND POINTS | - | - | USER COMMAND POINTS | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 | 42101 | Reset (software) processor |  | User | unit16 | W | 2100 | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 | 42102 | Clear all accumulated measurements (CAM) |  | User | unit16 | W | 2101 | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 | 42103 | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W | 12102 | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 | 42104 | Clear Peak Demand Element |  | User | unit16 | W | 12103 | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 | 42105 | Clear Peak Demand All |  | User | unit16 | W | 2104 | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 | 42106 | Reset to User Defaults |  | User | unit16 | W | 2105 | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - | USER CONFIG POINTS | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 | 42202 | Sliding or Fixed |  | Config | enum16 | R | 2201 | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 | 42203 | Demand Window | Min | Config | uint16 | R | 2202 | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 | 42204 | Volt Multiplier VINPUT1 |  | Config | float32 | R/W | 2203 | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | 42205 | [8 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 | 42206 | Volt Multiplier VINPUT2 |  | Config | float32 | R/W | 2205 | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | 42207 | [8 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 | 42208 | Service Type |  | Config | enum16 | R/W | 12207 | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 | 42209 | Snap MV Threshold | PER | Config | float32 | R/W | 2208 | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | 42210 | [8 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 | 42211 | Snap Rog Threshold | PER | Config | float32 | R/W | 2210 | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | 42212 | [8 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 | 42213 | Snap Volt Threshold | V | Config | float32 | R/W | 2212 | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | 42214 | [8 empty] | system |  |  | ALL
Communications Mode | 2214 | 42215 | Communications Mode |  | Config |  |  | 2214 | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 | 42216 | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W | 2215 | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | 42217 | [8 empty] | system |  |  | ALL
Voltage Input Element | 2217 | 42218 | Element Voltage Input |  | Config | enum16 | R/W | 12217 | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 | 42219 | CT1 RANGE | A | Config | float32 | R/W | 12218 | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | 42220 | [8 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 | 42221 | Voltage Reference for CT1 |  | Config | enum16 | R/W | 12220 | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 | 42222 | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W | 12221 | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | 42223 | [8 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 | 42224 | CT1 TYPE |  | Config | enum16 | R/W | 12223 | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 | 42225 | CT1 PHASE SHIFT | Deg | Config | float32 | R/W | 12224 | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | 42226 | [8 empty] | element |  |  | ALL
CH1 CT Sign | 2226 | 42227 | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W | 12226 | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 | 42228 | CT2 RANGE | A | Config | float32 | R/W | 12227 | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | 42229 | [8 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 | 42230 | Voltage Reference for CT2 |  | Config | enum16 | R/W | 12229 | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 | 42231 | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W | 12230 | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | 42232 | [8 empty] | element | >0 |  | ALL
CH2 CT type | 2232 | 42233 | CT2 TYPE |  | Config | enum16 | R/W | 12232 | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 | 42234 | CT2 PHASE SHIFT | Deg | Config | float32 | R/W | 12233 | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | 42235 | [8 empty] | element |  |  | ALL
CH2 CT Sign | 2235 | 42236 | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W | 12235 | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 | 42237 | CT3 INTEGER | A | Config | float32 | R/W | 12236 | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | 42238 | [8 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 | 42239 | Voltage Reference for CT3 |  | Config | enum16 | R/W | 12238 | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 | 42240 | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W | 12239 | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | 42241 | [8 empty] | element | >0 |  | ALL
CH3 CT type | 2241 | 42242 | CT3 TYPE |  | Config | enum16 | R/W | 12241 | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 | 42243 | CT3 PHASE SHIFT | Deg | Config | float32 | R/W | 12242 | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | 42244 | [8 empty] | element |  |  | ALL
CH3 CT Sign | 2244 | 42245 | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W | 12244 | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 | 42246 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 | 42247 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 | 42248 | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 | 42249 | PF Sign Convention |  | Config | uint16 | R/W | 2248 | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 | 42250 | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 | 42251 | BACnet UDP Port |  | Config | uint16 | R/W | 2250 | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 | 42252 | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 | 42253 | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | 42254 | [8 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 | 42261 | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | 42262 | [11 empty] | ALL
BACnet Max Info Frames | 2262 | 42263 | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 | 42264 | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 | 42265 | BBMD IP Address |  | Config | string(16) | R/W | 2264 | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | 42266 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | 42267 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | 42268 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | 42269 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | 42270 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | 42271 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | 42272 | [9 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 | 42273 | LCD/WebApp Read Password |  | Config | uint16 | R/W | 2272 | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 | 42274 | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 | 42275 | Customer Line frequency |  | Config | float | R/W | 2274 | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | 42276 | [10 empty] | Reserved | ALL
Communications Interface Configured | 2276 | 42277 | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 | 42278 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 | 42279 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 | 42280 | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 | 42281 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 | 42282 | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 | 42283 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 | 42284 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 | 42285 | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 | 42286 | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 | 42287 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 | 42288 | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 | 42289 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 | 42290 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 | 42291 | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 | 42292 | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | 42293 | [11 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 | 42294 | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | 42295 | [11 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 | 42296 | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 | 42297 | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - | METROLOGY POINTS | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 | 42301 | Displacement PF Avg Element | dPF | Metrology | float32 | R | 12300 | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | 42302 | [11 empty] | ALL
Displacement PF CH1 (MSW) | 2302 | 42303 | Displacement PF CH1 (A) | dPF | Metrology | float32 | R | 12302 | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | 42304 | [11 empty] | ALL
Displacement PF CH2 (MSW) | 2304 | 42305 | Displacement PF CH2 (B) | dPF | Metrology | float32 | R | 12304 | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | 42306 | [11 empty] | ALL
Displacement PF CH3 (MSW) | 2306 | 42307 | Displacement PF CH3 (C) | dPF | Metrology | float32 | R | 12306 | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | 42308 | [11 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 | 42309 | Avg Apparent PF Element | aPF | Metrology | float32 | R | 12308 | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | 42310 | [11 empty] | ALL
Apparent PF CH1 (MSW) | 2310 | 42311 | Apparent PF CH1 (A) | aPF | Metrology | float32 | R | 12310 | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | 42312 | [11 empty] | ALL
Apparent PF CH2 (MSW) | 2312 | 42313 | Apparent PF CH2 (B) | aPF | Metrology | float32 | R | 12312 | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | 42314 | [11 empty] | ALL
Apparent PF CH3 (MSW) | 2314 | 42315 | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R | 12314 | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | 42316 | [11 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 | 42317 | Distortion PF Avg Element | tPF | Metrology | float32 | R | 12316 | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | 42318 | [11 empty] | ALL
Distortion PF CH1 (MSW) | 2318 | 42319 | Distortion PF CH1 (A) | tPF | Metrology | float32 | R | 12318 | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | 42320 | [11 empty] | ALL
Distortion PF CH2 (MSW) | 2320 | 42321 | Distortion PF CH2 (B) | tPF | Metrology | float32 | R | 12320 | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | 42322 | [11 empty] | ALL
Distortion PF CH3 (MSW) | 2322 | 42323 | Distortion PF CH3 (C) | tPF | Metrology | float32 | R | 12322 | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | 42324 | [11 empty] | ALL
THD Avg Element (MSW) | 2324 | 42325 | THD Avg Element | % | Metrology | float32 | R | 12324 | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | 42326 | [11 empty] | ALL
THD CH1 (MSW) | 2326 | 42327 | THD CH1 (A) | % | Metrology | float32 | R | 12326 | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | 42328 | [11 empty] | ALL
THD CH2 (MSW) | 2328 | 42329 | THD CH2 (B) | % | Metrology | float32 | R | 12328 | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | 42330 | [11 empty] | ALL
THD CH3 (MSW) | 2330 | 42331 | THD CH3 (C) | % | Metrology | float32 | R | 12330 | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | 42332 | [11 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 | 42333 | Power Demand Max Interval Element | kW | Metrology | float32 | R | 12332 | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | 42334 | [11 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 | 42335 | Power Demand This Interval Element | kW | Metrology | float32 | R | 12334 | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | 42336 | [11 empty] | ALL
VA Peak Demand Element (MSW) | 2336 | 42337 | VA Demand Max Interval Element | kVA | Metrology | float32 | R | 12336 | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | 42338 | [11 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 | 42339 | VA Demand This Interval Element | kVA | Metrology | float32 | R | 12338 | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | 42340 | [11 empty] | ALL
Not Used | 2340 | 42341 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 | 42342 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 | 42343 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 | 42344 | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 | 42345 | Energy Net Sum Element | kWh | Metrology | float32 | R | 12344 | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | 42346 | [8 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 | 42347 | Energy Net CH1 | kWh | Metrology | float32 | R | 12346 | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | 42348 | [8 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 | 42349 | Energy Net CH2 | kWh | Metrology | float32 | R | 12348 | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | 42350 | [8 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 | 42351 | Energy Net CH3 | kWh | Metrology | float32 | R | 12350 | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | 42352 | [8 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 | 42353 | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R | 12352 | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | 42354 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 | 42355 | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R | 12354 | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | 42356 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 | 42357 | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R | 12356 | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | 42358 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 | 42359 | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R | 12358 | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | 42360 | [8 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 | 42361 | VARh Net Sum Element | kVArh | Metrology | float32 | R | 12360 | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | 42362 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 | 42363 | VARh Net CH1 | kVArh | Metrology | float32 | R | 12362 | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | 42364 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 | 42365 | VARh Net CH2 | kVArh | Metrology | float32 | R | 12364 | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | 42366 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 | 42367 | VARh Net CH3 | kVArh | Metrology | float32 | R | 12366 | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | 42368 | [8 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 | 42369 | Time Since Reset MSW | Sec | Metrology | uint32 |  | 2368 | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 | 42370 | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 | 42371 | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 | 42372 | CH1 Angle | Deg | Metrology | float32 | R | 12371 | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | 42373 | [8 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 | 42374 | CH2 Angle | Deg | Metrology | float32 | R | 12373 | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | 42375 | [8 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 | 42376 | CH3 Angle | Deg | Metrology | float32 | R | 12375 | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | 42377 | [11 empty] | ALL
Phase Chek System Status | 2377 | 42378 | System Phase Check Status |  | Metrology | bitfield16 | R | 2377 | BV | Phase Check System Status | system | 0,1 | 0 (All Channels OK), 1(Somewhere a channel is reading a dPF < 0.55), check register 2378 for each Element | ALL
Phase Chek Element Status | 2378 | 42379 | Element Phase Check Status |  | Metrology | bitfield16 | R | 12378 | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 | 42380 | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 | 42381 | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 | 42382 | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 | 42392 | Element Angle |  | Metrology | float | R | 12391 | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | 42393 | [11 empty] | ALL
PULSE INPUTS | - | - | PULSE INPUTS | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 | 42401 | Pulse Input 1 Enable |  | Config | uint16 | R/W | 2400 | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 | 42402 | Pulse Input 1 Scale Factor |  | Config | float32 | R/W | 2401 | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 | 42403 |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 | 42404 | Pulse Input 1 Units |  | Config | string(4) | R/W | 2403 | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 | 42405 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 | 42406 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 | 42407 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 | 42408 | Pulse Input 1 Accumulator |  | Metrology | float32 | R | 2407 | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | 42409 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 | 42410 | Pulse Input 1 Accumulator Clear |  | User | unit16 | W | 2409 | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 | 42411 | Pulse Input 2 Enable |  | Config | uint16 | R/W | 2410 | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 | 42412 | Pulse Input 2 Scale Factor |  | Config | float32 | R/W | 2411 | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | 42413 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 | 42414 | Pulse Input 2 Units |  | Config | string(4) | R/W | 2413 | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 | 42415 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 | 42416 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 | 42417 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 | 42418 | Pulse Input 2 Accumulator |  | Metrology | float32 | R | 2417 | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | 42419 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 | 42420 | Pulse Input 2 Accumulator Clear |  | User | unit16 | W | 2419 | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 | 42421 | Pulse Input 3 Enable |  | Config | uint16 | R/W | 2420 | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 | 42422 | Pulse Input 3 Scale Factor |  | Config | float32 | R/W | 2421 | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | 42423 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 | 42424 | Pulse Input 3 Units |  | Config | string(4) | R/W | 2423 | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 | 42425 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 | 42426 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 | 42427 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 | 42428 | Pulse Input 3 Accumulator |  | Metrology | float32 | R | 2427 | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | 42429 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 | 42430 | Pulse Input 3 Accumulator Clear |  | User |  | W | 2429 | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 | 42431 | Pulse Input 4 Enable |  | Config | uint16 | R/W | 2430 | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 | 42432 | Pulse Input 4 Scale Factor |  | Config | float32 | R/W | 2431 | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | 42433 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 | 42434 | Pulse Input 4 Units |  | Config | string(4) | R/W | 2433 | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 | 42435 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 | 42436 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 | 42437 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 | 42438 | Pulse Input 4 Accumulator |  | Metrology | float32 | R | 2437 | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | 42439 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 | 42440 | Pulse Input 4 Accumulator Clear |  | User | unit16 | W | 2439 | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - | ALARMS | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 | 42452 | State of Alarm |  | Metrology | uint16 | R/W | 2451 | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 | 42453 | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 | 42454 | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 | 42455 | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 | 42456 | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 | 42457 | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 | 42458 | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 | 42459 | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W | 2458 | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 | 42460 | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W | 2459 | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Range Vin1 L1N Under | 2460 | 42461 | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W | 2460 | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 | 42462 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2N Under | 2462 | 42463 | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W | 2462 | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 | 42464 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3N Under | 2464 | 42465 | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W | 2464 | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 | 42466 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L1L2 Under | 2466 | 42467 | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W | 2466 | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 | 42468 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2L3 Under | 2468 | 42469 | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W | 2468 | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 | 42470 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3L1 Under | 2470 | 42471 | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W | 2470 | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 | 42472 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin2 L1N Under | 2472 | 42473 | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W | 2472 | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 | 42474 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2N Under | 2474 | 42475 | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W | 2474 | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 | 42476 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3N Under | 2476 | 42477 | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W | 2476 | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 | 42478 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L1L2 Under | 2478 | 42479 | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W | 2478 | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 | 42480 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2L3 Under | 2480 | 42481 | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W | 2480 | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 | 42482 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3L1 Under | 2482 | 42483 | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W | 2482 | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 | 42484 | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 | 42485 | Voltage Alarm Persistence | Sec | Config | uint16 | R/W | 2484 | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 | 42486 | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R | 2485 | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 | 42487 | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 | 42488 | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R | 2487 | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 | 42489 | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 | 42490 | Real Time Clock MSW |  | Config | uint16 | R/W | 2489 | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 | 42491 | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - | USER CONFIG POINTS 2 | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 | 42602 | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 | 42603 | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 | 42604 | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 | 42605 | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 | 42606 | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 | 42607 | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 | 42608 | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 | 42609 | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 | 42610 | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 | 42611 | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 | 42612 | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 | 42613 | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 | 42614 | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 | 42615 | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 | 42616 | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 | 42617 | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 | 42618 | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 | 42619 | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 | 42620 | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 | 42621 | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 | 42622 | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 | 42623 | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 | 42624 | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 | 42625 | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 | 42626 | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 | 42627 | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 | 42628 | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 | 42629 | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 | 42630 | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 | 42631 | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 | 42632 | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 | 42633 | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 | 42634 | BACnet Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | 2634 | 42635 | BACnet Description 1 | [8 empty] | 2 Char |  | ALL
BACnet Description 2 | 2635 | 42636 | BACnet Description 2 | [8 empty] | 2 Char |  | ALL
BACnet Description 3 | 2636 | 42637 | BACnet Description 3 | [8 empty] | 2 Char |  | ALL
BACnet Description 4 | 2637 | 42638 | BACnet Description 4 | [8 empty] | 2 Char |  | ALL
BACnet Description 5 | 2638 | 42639 | BACnet Description 5 | [8 empty] | 2 Char |  | ALL
BACnet Description 6 | 2639 | 42640 | BACnet Description 6 | [8 empty] | 2 Char |  | ALL
BACnet Description 7 | 2640 | 42641 | BACnet Description 7 | [8 empty] | 2 Char |  | ALL
BACnet Description 8 | 2641 | 42642 | BACnet Description 8 | [8 empty] | 2 Char |  | ALL
BACnet Description 9 | 2642 | 42643 | BACnet Description 9 | [8 empty] | 2 Char |  | ALL
BACnet Description 10 | 2643 | 42644 | BACnet Description 10 | [8 empty] | 2 Char |  | ALL
BACnet Description 11 | 2644 | 42645 | BACnet Description 11 | [8 empty] | 2 Char |  | ALL
BACnet Description 12 | 2645 | 42646 | BACnet Description 12 | [8 empty] | 2 Char |  | ALL
BACnet Description 13 | 2646 | 42647 | BACnet Description 13 | [8 empty] | 2 Char |  | ALL
BACnet Description 14 | 2647 | 42648 | BACnet Description 14 | [8 empty] | 2 Char |  | ALL
BACnet Description 15 | 2648 | 42649 | BACnet Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
VERIS EMULATION LEGACY REGISTERS | - | - | VERIS EMULATION LEGACY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Veris Emulation Mode | 2200 | 42201 | Set to Veris Emulation Mode |  | Config | uint16 | R/W |  |  |  | system | 0-1 | 1 = Report Slave ID as Veris Model H8036 | ALL
kWh System LSW | 0 | 40001 | kWh System LSW | kWh | Veris | uint32 | R |  |  |  | element |  |  | ALL
kWh System MSW | 1 | 40002 | kWh System MSW | kWh | Veris |  | R |  |  |  | element |  |  | ALL
kW System | 2 | 40003 | kW System | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVAR System | 3 | 40004 | kVAR System | kVAR | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVA System | 4 | 40005 | kVA System | kVA | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF System | 5 | 40006 | Apparent PF System | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts Line to Line Avg | 6 | 40007 | Volts Line to Line Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts Line to Neutral Avg | 7 | 40008 | Volts Line to Neutral Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps System Avg | 8 | 40009 | Amps System Avg | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L1 | 9 | 40010 | kW L1 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L2 | 10 | 40011 | kW L2 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L3 | 11 | 40012 | kW L3 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L1 | 12 | 40013 | Apparent PF L1 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L2 | 13 | 40014 | Apparent PF L2 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L3 | 14 | 40015 | Apparent PF L3 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts L1 to L2 | 15 | 40016 | Volts L1 to L2 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to L3 | 16 | 40017 | Volts L2 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to L3 | 17 | 40018 | Volts L1 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to Neutral | 18 | 40019 | Volts L1 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to Neutral | 19 | 40020 | Volts L2 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L3 to Neutral | 20 | 40021 | Volts L3 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps L1 | 21 | 40022 | Amps L1 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L2 | 22 | 40023 | Amps L2 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L3 | 23 | 40024 | Amps L3 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW System Avg | 24 | 40025 | kW System Avg | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Now | 25 | 40026 | kW Demand Sys Now (was Min) | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Max | 26 | 40027 | kW Demand Sys Max | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL

## C
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS --> | 3
BACNET OBJECT FLOOR --> | 20000
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 | 41002 | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | 41003 | [8 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 | 41004 | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 | 41005 | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 | 41006 | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | 41007 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | 41008 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | 41009 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | 41010 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | 41011 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | 41012 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | 41013 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | 41014 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | 41015 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | 41016 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | 41017 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | 41018 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | 41019 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | 41020 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | 41021 | [8 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 | 41022 | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | 41023 | [8 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | 41024 | [8 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | 41025 | [8 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | 41026 | [8 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | 41027 | [8 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | 41028 | [8 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | 41029 | [8 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | 41030 | [8 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | 41031 | [8 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | 41032 | [8 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | 41033 | [8 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | 41034 | [8 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | 41035 | [8 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | 41036 | [8 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | 41037 | [8 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 | 41038 | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | 41039 | [8 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | 41040 | [8 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | 41041 | [8 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | 41042 | [8 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | 41043 | [8 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | 41044 | [8 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | 41045 | [8 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 | 41046 | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | 41047 | [8 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | 41048 | [8 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | 41049 | [8 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | 41050 | [8 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | 41051 | [8 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | 41052 | [8 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | 41053 | [8 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 | 41054 | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | 41055 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | 41056 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | 41057 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | 41058 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | 41059 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | 41060 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | 41061 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | 41062 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | 41063 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | 41064 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | 41065 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | 41066 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | 41067 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | 41068 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | 41069 | [8 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 | 41070 | Modbus Device Address |  |  | unit16 | R/W | 1069 | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | 41071 | [8 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 | 41072 | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 | 41073 | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 | 41074 | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | 41075 | [8 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | 41076 | [8 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | 41077 | [8 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 | 41078 | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 | 41079 | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 | 41080 | IP Address |  |  | string(8) | R/W | 1079 | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | 41081 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | 41082 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | 41083 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | 41084 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | 41085 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | 41086 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | 41087 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 | 41088 | Netmask |  |  | string(8) | R/W | 1087 | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | 41089 | [8 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | 41090 | [8 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | 41091 | [8 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | 41092 | [8 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | 41093 | [8 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | 41094 | [8 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | 41095 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 | 41096 | Gateway |  |  | string(8) | R/W | 1095 | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | 41097 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | 41098 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | 41099 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | 41100 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | 41101 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | 41102 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | 41103 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 | 41104 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | 41105 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | 41106 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | 41107 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | 41108 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | 41109 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | 41110 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | 41111 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 | 41112 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | 41113 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | 41114 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | 41115 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | 41116 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | 41117 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | 41118 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | 41119 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 | 41120 | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | 41121 | [8 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | 41122 | [8 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | 41123 | [8 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 | 41124 | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | 41125 | [9 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 | 41126 | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 | 41127 | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 | 41128 | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | 41129 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | 41130 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | 41131 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 | 41132 | Interface baud rate in bits per second |  |  | uint32 | R/W | 1131 | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | 41133 | [8 empty] | system |  |  | ALL
SERIAL BITS | 1133 | 41134 | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 | 41135 | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 | 41136 | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 | 41137 | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 | 41138 | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 | 41139 | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 | 41140 | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 | 41141 | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 | 41142 | Current Avg Element | A | Metrology | float32 | R | 21141 | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | 41143 | [8 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 | 41144 | Current CH1 (A) | A | Metrology | float32 | R | 21143 | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | 41145 | [8 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 | 41146 | Current CH2 (B) | A | Metrology | float32 | R | 21145 | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | 41147 | [8 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 | 41148 | Current CH3 (C) | A | Metrology | float32 | R | 21147 | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | 41149 | [8 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 | 41150 | Voltage L to N Avg Element | V | Metrology | float32 | R | 21149 | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | 41151 | [8 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 | 41152 | Voltage L1 to N (AN) | V | Metrology | float32 | R | 21151 | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | 41153 | [8 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 | 41154 | Voltage L2 to N (BN) | V | Metrology | float32 | R | 21153 | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | 41155 | [8 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 | 41156 | Voltage L3 to N (CN) | V | Metrology | float32 | R | 21155 | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | 41157 | [8 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 | 41158 | Voltage L to L Avg Element | V | Metrology | float32 | R | 21157 | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | 41159 | [8 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 | 41160 | Voltage L1 to L2 (AB) | V | Metrology | float32 | R | 21159 | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | 41161 | [8 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 | 41162 | Voltage L2 to L3 (BC) | V | Metrology | float32 | R | 21161 | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | 41163 | [8 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 | 41164 | Voltage L3 to L1 (CA) | V | Metrology | float32 | R | 21163 | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | 41165 | [8 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 | 41166 | Line Frequency | Hz | Metrology | float32 | R | 21165 | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | 41167 | [8 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 | 41168 | Power Sum Element | kW | Metrology | float32 | R | 21167 | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | 41169 | [8 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 | 41170 | Power CH1 (A) | kW | Metrology | float32 | R | 21169 | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | 41171 | [8 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 | 41172 | Power CH2 (B) | kW | Metrology | float32 | R | 21171 | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | 41173 | [8 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 | 41174 | Power CH3 (C) | kW | Metrology | float32 | R | 21173 | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | 41175 | [8 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 | 41176 | VA Sum Element | kVA | Metrology | float32 | R | 21175 | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | 41177 | [8 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 | 41178 | VA CH1 (A) | kVA | Metrology | float32 | R | 21177 | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | 41179 | [8 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 | 41180 | VA CH2 (B) | kVA | Metrology | float32 | R | 21179 | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | 41181 | [8 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 | 41182 | VA CH3 (C) | kVA | Metrology | float32 | R | 21181 | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | 41183 | [8 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 | 41184 | VAR Sum Element | kVAr | Metrology | float32 | R | 21183 | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | 41185 | [8 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 | 41186 | VAR CH1 (A) | kVAr | Metrology | float32 | R | 21185 | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | 41187 | [8 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 | 41188 | VAR CH2 (B) | kVAr | Metrology | float32 | R | 21187 | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | 41189 | [8 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 | 41190 | VAR CH3 (C) | kVAr | Metrology | float32 | R | 21189 | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | 41191 | [8 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 | 41192 | Apparent PF Avg Element | PF | Metrology | float32 | R | 21191 | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | 41193 | [8 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 | 41194 | Apparent PF CH1 (A) | PF | Metrology | float32 | R | 21193 | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | 41195 | [8 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 | 41196 | Apparent PF CH2 (B) | PF | Metrology | float32 | R | 21195 | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | 41197 | [8 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 | 41198 | Apparent PF CH3 ( C) | PF | Metrology | float32 | R | 21197 | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | 41199 | [8 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 | 41200 | Exported Energy Sum Element | kWh | Metrology | float32 | R | 21199 | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | 41201 | [8 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 | 41202 | Exported Energy CH1 (A) | kWh | Metrology | float32 | R | 21201 | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | 41203 | [8 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 | 41204 | Exported Energy CH2 (B) | kWh | Metrology | float32 | R | 21203 | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | 41205 | [8 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 | 41206 | Exported Energy CH3 (C) | kWh | Metrology | float32 | R | 21205 | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | 41207 | [8 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 | 41208 | Imported Energy Sum Element | kWh | Metrology | float32 | R | 21207 | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | 41209 | [8 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 | 41210 | Imported Energy CH1 (A) | kWh | Metrology | float32 | R | 21209 | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | 41211 | [8 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 | 41212 | Imported Energy CH2 (B) | kWh | Metrology | float32 | R | 21211 | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | 41213 | [8 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 | 41214 | Imported Energy CH3 (C) | kWh | Metrology | float32 | R | 21213 | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | 41215 | [8 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 | 41216 | Exported VAh Sum Element | kVAh | Metrology | float32 | R | 21215 | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | 41217 | [8 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 | 41218 | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R | 21217 | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | 41219 | [8 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 | 41220 | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R | 21219 | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | 41221 | [8 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 | 41222 | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R | 21221 | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | 41223 | [8 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 | 41224 | Imported VAh Sum Element | kVAh | Metrology | float32 | R | 21223 | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | 41225 | [8 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 | 41226 | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R | 21225 | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | 41227 | [8 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 | 41228 | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R | 21227 | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | 41229 | [8 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 | 41230 | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R | 21229 | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | 41231 | [8 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 | 41232 | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R | 21231 | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | 41233 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 | 41234 | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R | 21233 | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | 41235 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 | 41236 | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R | 21235 | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | 41237 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 | 41238 | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R | 21237 | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | 41239 | [8 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 | 41240 | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R | 21239 | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | 41241 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 | 41242 | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R | 21241 | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | 41243 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 | 41244 | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R | 21243 | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | 41245 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 | 41246 | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R | 21245 | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | 41247 | [8 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 | 41248 | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R | 21247 | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | 41249 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 | 41250 | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R | 21249 | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | 41251 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 | 41252 | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R | 21251 | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | 41253 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 | 41254 | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R | 21253 | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | 41255 | [8 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 | 41256 | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R | 21255 | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | 41257 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 | 41258 | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R | 21257 | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | 41259 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 | 41260 | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R | 21259 | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | 41261 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 | 41262 | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R | 21261 | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | 41263 | [8 empty] | element |  |  | ALL
Events MSW | 1263 | 41264 | Events MSW |  |  | bitfield32 | R | 1263 | AI | Events | system |  |  | ALL
Events LSW | 1264 | 41265 | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 | 41266 | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 | 41267 | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
FACTORY REGISTERS | - | - | FACTORY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Factory Unlock Register | 2000 | 42001 | Factory Unlock Register |  | Factory | unit16 | R/W |  |  |  | system |  | Reserved | ALL
Factory Reset | 2001 | 42002 | Factory Reset |  | Factory | unit16 | R/W |  |  |  | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
OEM Vendor ID | 2002 | 42003 | OEM Vendor ID |  | Factory | unit16 | R |  |  |  | system |  | Reserved | ALL
FACTORY_CONFIG | 2003 | 42004 | Factory Config |  | Factory | unit16 | R |  |  |  | system | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable | ALL
USER COMMAND POINTS | - | - | USER COMMAND POINTS | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 | 42101 | Reset (software) processor |  | User | unit16 | W | 2100 | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 | 42102 | Clear all accumulated measurements (CAM) |  | User | unit16 | W | 2101 | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 | 42103 | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W | 22102 | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 | 42104 | Clear Peak Demand Element |  | User | unit16 | W | 22103 | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 | 42105 | Clear Peak Demand All |  | User | unit16 | W | 2104 | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 | 42106 | Reset to User Defaults |  | User | unit16 | W | 2105 | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - | USER CONFIG POINTS | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 | 42202 | Sliding or Fixed |  | Config | enum16 | R | 2201 | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 | 42203 | Demand Window | Min | Config | uint16 | R | 2202 | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 | 42204 | Volt Multiplier VINPUT1 |  | Config | float32 | R/W | 2203 | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | 42205 | [8 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 | 42206 | Volt Multiplier VINPUT2 |  | Config | float32 | R/W | 2205 | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | 42207 | [8 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 | 42208 | Service Type |  | Config | enum16 | R/W | 22207 | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 | 42209 | Snap MV Threshold | PER | Config | float32 | R/W | 2208 | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | 42210 | [8 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 | 42211 | Snap Rog Threshold | PER | Config | float32 | R/W | 2210 | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | 42212 | [8 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 | 42213 | Snap Volt Threshold | V | Config | float32 | R/W | 2212 | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | 42214 | [8 empty] | system |  |  | ALL
Communications Mode | 2214 | 42215 | Communications Mode |  | Config |  |  | 2214 | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 | 42216 | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W | 2215 | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | 42217 | [8 empty] | system |  |  | ALL
Voltage Input Element | 2217 | 42218 | Element Voltage Input |  | Config | enum16 | R/W | 22217 | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 | 42219 | CT1 RANGE | A | Config | float32 | R/W | 22218 | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | 42220 | [8 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 | 42221 | Voltage Reference for CT1 |  | Config | enum16 | R/W | 22220 | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 | 42222 | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W | 22221 | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | 42223 | [8 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 | 42224 | CT1 TYPE |  | Config | enum16 | R/W | 22223 | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 | 42225 | CT1 PHASE SHIFT | Deg | Config | float32 | R/W | 22224 | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | 42226 | [8 empty] | element |  |  | ALL
CH1 CT Sign | 2226 | 42227 | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W | 22226 | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 | 42228 | CT2 RANGE | A | Config | float32 | R/W | 22227 | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | 42229 | [8 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 | 42230 | Voltage Reference for CT2 |  | Config | enum16 | R/W | 22229 | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 | 42231 | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W | 22230 | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | 42232 | [8 empty] | element | >0 |  | ALL
CH2 CT type | 2232 | 42233 | CT2 TYPE |  | Config | enum16 | R/W | 22232 | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 | 42234 | CT2 PHASE SHIFT | Deg | Config | float32 | R/W | 22233 | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | 42235 | [8 empty] | element |  |  | ALL
CH2 CT Sign | 2235 | 42236 | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W | 22235 | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 | 42237 | CT3 INTEGER | A | Config | float32 | R/W | 22236 | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | 42238 | [8 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 | 42239 | Voltage Reference for CT3 |  | Config | enum16 | R/W | 22238 | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 | 42240 | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W | 22239 | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | 42241 | [8 empty] | element | >0 |  | ALL
CH3 CT type | 2241 | 42242 | CT3 TYPE |  | Config | enum16 | R/W | 22241 | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 | 42243 | CT3 PHASE SHIFT | Deg | Config | float32 | R/W | 22242 | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | 42244 | [8 empty] | element |  |  | ALL
CH3 CT Sign | 2244 | 42245 | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W | 22244 | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 | 42246 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 | 42247 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 | 42248 | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 | 42249 | PF Sign Convention |  | Config | uint16 | R/W | 2248 | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 | 42250 | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 | 42251 | BACnet UDP Port |  | Config | uint16 | R/W | 2250 | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 | 42252 | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 | 42253 | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | 42254 | [8 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 | 42261 | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | 42262 | [11 empty] | ALL
BACnet Max Info Frames | 2262 | 42263 | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 | 42264 | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 | 42265 | BBMD IP Address |  | Config | string(16) | R/W | 2264 | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | 42266 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | 42267 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | 42268 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | 42269 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | 42270 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | 42271 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | 42272 | [9 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 | 42273 | LCD/WebApp Read Password |  | Config | uint16 | R/W | 2272 | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 | 42274 | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 | 42275 | Customer Line frequency |  | Config | float | R/W | 2274 | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | 42276 | [10 empty] | Reserved | ALL
Communications Interface Configured | 2276 | 42277 | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 | 42278 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 | 42279 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 | 42280 | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 | 42281 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 | 42282 | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 | 42283 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 | 42284 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 | 42285 | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 | 42286 | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 | 42287 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 | 42288 | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 | 42289 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 | 42290 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 | 42291 | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 | 42292 | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | 42293 | [11 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 | 42294 | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | 42295 | [11 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 | 42296 | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 | 42297 | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - | METROLOGY POINTS | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 | 42301 | Displacement PF Avg Element | dPF | Metrology | float32 | R | 22300 | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | 42302 | [11 empty] | ALL
Displacement PF CH1 (MSW) | 2302 | 42303 | Displacement PF CH1 (A) | dPF | Metrology | float32 | R | 22302 | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | 42304 | [11 empty] | ALL
Displacement PF CH2 (MSW) | 2304 | 42305 | Displacement PF CH2 (B) | dPF | Metrology | float32 | R | 22304 | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | 42306 | [11 empty] | ALL
Displacement PF CH3 (MSW) | 2306 | 42307 | Displacement PF CH3 (C) | dPF | Metrology | float32 | R | 22306 | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | 42308 | [11 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 | 42309 | Avg Apparent PF Element | aPF | Metrology | float32 | R | 22308 | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | 42310 | [11 empty] | ALL
Apparent PF CH1 (MSW) | 2310 | 42311 | Apparent PF CH1 (A) | aPF | Metrology | float32 | R | 22310 | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | 42312 | [11 empty] | ALL
Apparent PF CH2 (MSW) | 2312 | 42313 | Apparent PF CH2 (B) | aPF | Metrology | float32 | R | 22312 | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | 42314 | [11 empty] | ALL
Apparent PF CH3 (MSW) | 2314 | 42315 | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R | 22314 | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | 42316 | [11 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 | 42317 | Distortion PF Avg Element | tPF | Metrology | float32 | R | 22316 | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | 42318 | [11 empty] | ALL
Distortion PF CH1 (MSW) | 2318 | 42319 | Distortion PF CH1 (A) | tPF | Metrology | float32 | R | 22318 | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | 42320 | [11 empty] | ALL
Distortion PF CH2 (MSW) | 2320 | 42321 | Distortion PF CH2 (B) | tPF | Metrology | float32 | R | 22320 | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | 42322 | [11 empty] | ALL
Distortion PF CH3 (MSW) | 2322 | 42323 | Distortion PF CH3 (C) | tPF | Metrology | float32 | R | 22322 | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | 42324 | [11 empty] | ALL
THD Avg Element (MSW) | 2324 | 42325 | THD Avg Element | % | Metrology | float32 | R | 22324 | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | 42326 | [11 empty] | ALL
THD CH1 (MSW) | 2326 | 42327 | THD CH1 (A) | % | Metrology | float32 | R | 22326 | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | 42328 | [11 empty] | ALL
THD CH2 (MSW) | 2328 | 42329 | THD CH2 (B) | % | Metrology | float32 | R | 22328 | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | 42330 | [11 empty] | ALL
THD CH3 (MSW) | 2330 | 42331 | THD CH3 (C) | % | Metrology | float32 | R | 22330 | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | 42332 | [11 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 | 42333 | Power Demand Max Interval Element | kW | Metrology | float32 | R | 22332 | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | 42334 | [11 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 | 42335 | Power Demand This Interval Element | kW | Metrology | float32 | R | 22334 | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | 42336 | [11 empty] | ALL
VA Peak Demand Element (MSW) | 2336 | 42337 | VA Demand Max Interval Element | kVA | Metrology | float32 | R | 22336 | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | 42338 | [11 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 | 42339 | VA Demand This Interval Element | kVA | Metrology | float32 | R | 22338 | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | 42340 | [11 empty] | ALL
Not Used | 2340 | 42341 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 | 42342 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 | 42343 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 | 42344 | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 | 42345 | Energy Net Sum Element | kWh | Metrology | float32 | R | 22344 | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | 42346 | [8 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 | 42347 | Energy Net CH1 | kWh | Metrology | float32 | R | 22346 | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | 42348 | [8 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 | 42349 | Energy Net CH2 | kWh | Metrology | float32 | R | 22348 | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | 42350 | [8 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 | 42351 | Energy Net CH3 | kWh | Metrology | float32 | R | 22350 | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | 42352 | [8 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 | 42353 | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R | 22352 | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | 42354 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 | 42355 | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R | 22354 | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | 42356 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 | 42357 | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R | 22356 | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | 42358 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 | 42359 | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R | 22358 | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | 42360 | [8 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 | 42361 | VARh Net Sum Element | kVArh | Metrology | float32 | R | 22360 | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | 42362 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 | 42363 | VARh Net CH1 | kVArh | Metrology | float32 | R | 22362 | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | 42364 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 | 42365 | VARh Net CH2 | kVArh | Metrology | float32 | R | 22364 | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | 42366 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 | 42367 | VARh Net CH3 | kVArh | Metrology | float32 | R | 22366 | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | 42368 | [8 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 | 42369 | Time Since Reset MSW | Sec | Metrology | uint32 |  | 2368 | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 | 42370 | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 | 42371 | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 | 42372 | CH1 Angle | Deg | Metrology | float32 | R | 22371 | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | 42373 | [8 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 | 42374 | CH2 Angle | Deg | Metrology | float32 | R | 22373 | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | 42375 | [8 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 | 42376 | CH3 Angle | Deg | Metrology | float32 | R | 22375 | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | 42377 | [11 empty] | ALL
Phase Chek System Status | 2377 | 42378 | System Phase Check Status |  | Metrology | bitfield16 | R | 2377 | BV | Phase Check System Status | system | 0,1 | 0 (All Channels OK), 1(Somewhere a channel is reading a dPF < 0.55), check register 2378 for each Element | ALL
Phase Chek Element Status | 2378 | 42379 | Element Phase Check Status |  | Metrology | bitfield16 | R | 22378 | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 | 42380 | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 | 42381 | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 | 42382 | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 | 42392 | Element Angle |  | Metrology | float | R | 22391 | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | 42393 | [11 empty] | ALL
PULSE INPUTS | - | - | PULSE INPUTS | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 | 42401 | Pulse Input 1 Enable |  | Config | uint16 | R/W | 2400 | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 | 42402 | Pulse Input 1 Scale Factor |  | Config | float32 | R/W | 2401 | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 | 42403 |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 | 42404 | Pulse Input 1 Units |  | Config | string(4) | R/W | 2403 | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 | 42405 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 | 42406 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 | 42407 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 | 42408 | Pulse Input 1 Accumulator |  | Metrology | float32 | R | 2407 | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | 42409 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 | 42410 | Pulse Input 1 Accumulator Clear |  | User | unit16 | W | 2409 | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 | 42411 | Pulse Input 2 Enable |  | Config | uint16 | R/W | 2410 | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 | 42412 | Pulse Input 2 Scale Factor |  | Config | float32 | R/W | 2411 | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | 42413 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 | 42414 | Pulse Input 2 Units |  | Config | string(4) | R/W | 2413 | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 | 42415 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 | 42416 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 | 42417 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 | 42418 | Pulse Input 2 Accumulator |  | Metrology | float32 | R | 2417 | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | 42419 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 | 42420 | Pulse Input 2 Accumulator Clear |  | User | unit16 | W | 2419 | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 | 42421 | Pulse Input 3 Enable |  | Config | uint16 | R/W | 2420 | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 | 42422 | Pulse Input 3 Scale Factor |  | Config | float32 | R/W | 2421 | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | 42423 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 | 42424 | Pulse Input 3 Units |  | Config | string(4) | R/W | 2423 | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 | 42425 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 | 42426 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 | 42427 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 | 42428 | Pulse Input 3 Accumulator |  | Metrology | float32 | R | 2427 | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | 42429 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 | 42430 | Pulse Input 3 Accumulator Clear |  | User |  | W | 2429 | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 | 42431 | Pulse Input 4 Enable |  | Config | uint16 | R/W | 2430 | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 | 42432 | Pulse Input 4 Scale Factor |  | Config | float32 | R/W | 2431 | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | 42433 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 | 42434 | Pulse Input 4 Units |  | Config | string(4) | R/W | 2433 | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 | 42435 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 | 42436 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 | 42437 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 | 42438 | Pulse Input 4 Accumulator |  | Metrology | float32 | R | 2437 | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | 42439 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 | 42440 | Pulse Input 4 Accumulator Clear |  | User | unit16 | W | 2439 | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - | ALARMS | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 | 42452 | State of Alarm |  | Metrology | uint16 | R/W | 2451 | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 | 42453 | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 | 42454 | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 | 42455 | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 | 42456 | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 | 42457 | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 | 42458 | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 | 42459 | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W | 2458 | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 | 42460 | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W | 2459 | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Range Vin1 L1N Under | 2460 | 42461 | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W | 2460 | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 | 42462 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2N Under | 2462 | 42463 | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W | 2462 | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 | 42464 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3N Under | 2464 | 42465 | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W | 2464 | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 | 42466 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L1L2 Under | 2466 | 42467 | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W | 2466 | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 | 42468 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2L3 Under | 2468 | 42469 | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W | 2468 | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 | 42470 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3L1 Under | 2470 | 42471 | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W | 2470 | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 | 42472 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin2 L1N Under | 2472 | 42473 | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W | 2472 | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 | 42474 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2N Under | 2474 | 42475 | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W | 2474 | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 | 42476 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3N Under | 2476 | 42477 | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W | 2476 | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 | 42478 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L1L2 Under | 2478 | 42479 | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W | 2478 | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 | 42480 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2L3 Under | 2480 | 42481 | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W | 2480 | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 | 42482 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3L1 Under | 2482 | 42483 | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W | 2482 | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 | 42484 | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 | 42485 | Voltage Alarm Persistence | Sec | Config | uint16 | R/W | 2484 | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 | 42486 | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R | 2485 | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 | 42487 | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 | 42488 | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R | 2487 | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 | 42489 | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 | 42490 | Real Time Clock MSW |  | Config | uint16 | R/W | 2489 | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 | 42491 | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - | USER CONFIG POINTS 2 | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 | 42602 | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 | 42603 | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 | 42604 | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 | 42605 | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 | 42606 | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 | 42607 | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 | 42608 | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 | 42609 | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 | 42610 | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 | 42611 | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 | 42612 | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 | 42613 | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 | 42614 | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 | 42615 | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 | 42616 | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 | 42617 | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 | 42618 | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 | 42619 | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 | 42620 | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 | 42621 | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 | 42622 | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 | 42623 | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 | 42624 | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 | 42625 | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 | 42626 | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 | 42627 | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 | 42628 | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 | 42629 | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 | 42630 | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 | 42631 | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 | 42632 | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 | 42633 | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 | 42634 | BACnet Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | 2634 | 42635 | BACnet Description 1 | [8 empty] | 2 Char |  | ALL
BACnet Description 2 | 2635 | 42636 | BACnet Description 2 | [8 empty] | 2 Char |  | ALL
BACnet Description 3 | 2636 | 42637 | BACnet Description 3 | [8 empty] | 2 Char |  | ALL
BACnet Description 4 | 2637 | 42638 | BACnet Description 4 | [8 empty] | 2 Char |  | ALL
BACnet Description 5 | 2638 | 42639 | BACnet Description 5 | [8 empty] | 2 Char |  | ALL
BACnet Description 6 | 2639 | 42640 | BACnet Description 6 | [8 empty] | 2 Char |  | ALL
BACnet Description 7 | 2640 | 42641 | BACnet Description 7 | [8 empty] | 2 Char |  | ALL
BACnet Description 8 | 2641 | 42642 | BACnet Description 8 | [8 empty] | 2 Char |  | ALL
BACnet Description 9 | 2642 | 42643 | BACnet Description 9 | [8 empty] | 2 Char |  | ALL
BACnet Description 10 | 2643 | 42644 | BACnet Description 10 | [8 empty] | 2 Char |  | ALL
BACnet Description 11 | 2644 | 42645 | BACnet Description 11 | [8 empty] | 2 Char |  | ALL
BACnet Description 12 | 2645 | 42646 | BACnet Description 12 | [8 empty] | 2 Char |  | ALL
BACnet Description 13 | 2646 | 42647 | BACnet Description 13 | [8 empty] | 2 Char |  | ALL
BACnet Description 14 | 2647 | 42648 | BACnet Description 14 | [8 empty] | 2 Char |  | ALL
BACnet Description 15 | 2648 | 42649 | BACnet Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
VERIS EMULATION LEGACY REGISTERS | - | - | VERIS EMULATION LEGACY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Veris Emulation Mode | 2200 | 42201 | Set to Veris Emulation Mode |  | Config | uint16 | R/W |  |  |  | system | 0-1 | 1 = Report Slave ID as Veris Model H8036 | ALL
kWh System LSW | 0 | 40001 | kWh System LSW | kWh | Veris | uint32 | R |  |  |  | element |  |  | ALL
kWh System MSW | 1 | 40002 | kWh System MSW | kWh | Veris |  | R |  |  |  | element |  |  | ALL
kW System | 2 | 40003 | kW System | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVAR System | 3 | 40004 | kVAR System | kVAR | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVA System | 4 | 40005 | kVA System | kVA | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF System | 5 | 40006 | Apparent PF System | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts Line to Line Avg | 6 | 40007 | Volts Line to Line Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts Line to Neutral Avg | 7 | 40008 | Volts Line to Neutral Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps System Avg | 8 | 40009 | Amps System Avg | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L1 | 9 | 40010 | kW L1 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L2 | 10 | 40011 | kW L2 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L3 | 11 | 40012 | kW L3 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L1 | 12 | 40013 | Apparent PF L1 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L2 | 13 | 40014 | Apparent PF L2 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L3 | 14 | 40015 | Apparent PF L3 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts L1 to L2 | 15 | 40016 | Volts L1 to L2 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to L3 | 16 | 40017 | Volts L2 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to L3 | 17 | 40018 | Volts L1 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to Neutral | 18 | 40019 | Volts L1 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to Neutral | 19 | 40020 | Volts L2 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L3 to Neutral | 20 | 40021 | Volts L3 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps L1 | 21 | 40022 | Amps L1 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L2 | 22 | 40023 | Amps L2 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L3 | 23 | 40024 | Amps L3 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW System Avg | 24 | 40025 | kW System Avg | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Now | 25 | 40026 | kW Demand Sys Now (was Min) | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Max | 26 | 40027 | kW Demand Sys Max | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL

## D
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS --> | 4
BACNET OBJECT FLOOR --> | 30000
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 | 41002 | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | 41003 | [8 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 | 41004 | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 | 41005 | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 | 41006 | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | 41007 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | 41008 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | 41009 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | 41010 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | 41011 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | 41012 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | 41013 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | 41014 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | 41015 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | 41016 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | 41017 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | 41018 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | 41019 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | 41020 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | 41021 | [8 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 | 41022 | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | 41023 | [8 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | 41024 | [8 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | 41025 | [8 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | 41026 | [8 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | 41027 | [8 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | 41028 | [8 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | 41029 | [8 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | 41030 | [8 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | 41031 | [8 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | 41032 | [8 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | 41033 | [8 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | 41034 | [8 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | 41035 | [8 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | 41036 | [8 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | 41037 | [8 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 | 41038 | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | 41039 | [8 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | 41040 | [8 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | 41041 | [8 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | 41042 | [8 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | 41043 | [8 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | 41044 | [8 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | 41045 | [8 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 | 41046 | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | 41047 | [8 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | 41048 | [8 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | 41049 | [8 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | 41050 | [8 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | 41051 | [8 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | 41052 | [8 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | 41053 | [8 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 | 41054 | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | 41055 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | 41056 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | 41057 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | 41058 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | 41059 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | 41060 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | 41061 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | 41062 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | 41063 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | 41064 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | 41065 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | 41066 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | 41067 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | 41068 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | 41069 | [8 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 | 41070 | Modbus Device Address |  |  | unit16 | R/W | 1069 | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | 41071 | [8 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 | 41072 | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 | 41073 | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 | 41074 | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | 41075 | [8 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | 41076 | [8 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | 41077 | [8 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 | 41078 | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 | 41079 | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 | 41080 | IP Address |  |  | string(8) | R/W | 1079 | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | 41081 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | 41082 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | 41083 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | 41084 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | 41085 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | 41086 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | 41087 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 | 41088 | Netmask |  |  | string(8) | R/W | 1087 | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | 41089 | [8 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | 41090 | [8 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | 41091 | [8 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | 41092 | [8 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | 41093 | [8 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | 41094 | [8 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | 41095 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 | 41096 | Gateway |  |  | string(8) | R/W | 1095 | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | 41097 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | 41098 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | 41099 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | 41100 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | 41101 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | 41102 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | 41103 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 | 41104 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | 41105 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | 41106 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | 41107 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | 41108 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | 41109 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | 41110 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | 41111 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 | 41112 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | 41113 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | 41114 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | 41115 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | 41116 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | 41117 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | 41118 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | 41119 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 | 41120 | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | 41121 | [8 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | 41122 | [8 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | 41123 | [8 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 | 41124 | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | 41125 | [9 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 | 41126 | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 | 41127 | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 | 41128 | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | 41129 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | 41130 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | 41131 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 | 41132 | Interface baud rate in bits per second |  |  | uint32 | R/W | 1131 | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | 41133 | [8 empty] | system |  |  | ALL
SERIAL BITS | 1133 | 41134 | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 | 41135 | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 | 41136 | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 | 41137 | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 | 41138 | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 | 41139 | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 | 41140 | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 | 41141 | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 | 41142 | Current Avg Element | A | Metrology | float32 | R | 31141 | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | 41143 | [8 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 | 41144 | Current CH1 (A) | A | Metrology | float32 | R | 31143 | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | 41145 | [8 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 | 41146 | Current CH2 (B) | A | Metrology | float32 | R | 31145 | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | 41147 | [8 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 | 41148 | Current CH3 (C) | A | Metrology | float32 | R | 31147 | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | 41149 | [8 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 | 41150 | Voltage L to N Avg Element | V | Metrology | float32 | R | 31149 | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | 41151 | [8 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 | 41152 | Voltage L1 to N (AN) | V | Metrology | float32 | R | 31151 | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | 41153 | [8 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 | 41154 | Voltage L2 to N (BN) | V | Metrology | float32 | R | 31153 | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | 41155 | [8 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 | 41156 | Voltage L3 to N (CN) | V | Metrology | float32 | R | 31155 | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | 41157 | [8 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 | 41158 | Voltage L to L Avg Element | V | Metrology | float32 | R | 31157 | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | 41159 | [8 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 | 41160 | Voltage L1 to L2 (AB) | V | Metrology | float32 | R | 31159 | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | 41161 | [8 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 | 41162 | Voltage L2 to L3 (BC) | V | Metrology | float32 | R | 31161 | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | 41163 | [8 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 | 41164 | Voltage L3 to L1 (CA) | V | Metrology | float32 | R | 31163 | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | 41165 | [8 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 | 41166 | Line Frequency | Hz | Metrology | float32 | R | 31165 | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | 41167 | [8 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 | 41168 | Power Sum Element | kW | Metrology | float32 | R | 31167 | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | 41169 | [8 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 | 41170 | Power CH1 (A) | kW | Metrology | float32 | R | 31169 | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | 41171 | [8 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 | 41172 | Power CH2 (B) | kW | Metrology | float32 | R | 31171 | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | 41173 | [8 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 | 41174 | Power CH3 (C) | kW | Metrology | float32 | R | 31173 | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | 41175 | [8 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 | 41176 | VA Sum Element | kVA | Metrology | float32 | R | 31175 | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | 41177 | [8 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 | 41178 | VA CH1 (A) | kVA | Metrology | float32 | R | 31177 | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | 41179 | [8 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 | 41180 | VA CH2 (B) | kVA | Metrology | float32 | R | 31179 | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | 41181 | [8 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 | 41182 | VA CH3 (C) | kVA | Metrology | float32 | R | 31181 | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | 41183 | [8 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 | 41184 | VAR Sum Element | kVAr | Metrology | float32 | R | 31183 | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | 41185 | [8 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 | 41186 | VAR CH1 (A) | kVAr | Metrology | float32 | R | 31185 | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | 41187 | [8 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 | 41188 | VAR CH2 (B) | kVAr | Metrology | float32 | R | 31187 | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | 41189 | [8 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 | 41190 | VAR CH3 (C) | kVAr | Metrology | float32 | R | 31189 | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | 41191 | [8 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 | 41192 | Apparent PF Avg Element | PF | Metrology | float32 | R | 31191 | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | 41193 | [8 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 | 41194 | Apparent PF CH1 (A) | PF | Metrology | float32 | R | 31193 | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | 41195 | [8 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 | 41196 | Apparent PF CH2 (B) | PF | Metrology | float32 | R | 31195 | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | 41197 | [8 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 | 41198 | Apparent PF CH3 ( C) | PF | Metrology | float32 | R | 31197 | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | 41199 | [8 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 | 41200 | Exported Energy Sum Element | kWh | Metrology | float32 | R | 31199 | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | 41201 | [8 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 | 41202 | Exported Energy CH1 (A) | kWh | Metrology | float32 | R | 31201 | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | 41203 | [8 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 | 41204 | Exported Energy CH2 (B) | kWh | Metrology | float32 | R | 31203 | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | 41205 | [8 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 | 41206 | Exported Energy CH3 (C) | kWh | Metrology | float32 | R | 31205 | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | 41207 | [8 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 | 41208 | Imported Energy Sum Element | kWh | Metrology | float32 | R | 31207 | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | 41209 | [8 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 | 41210 | Imported Energy CH1 (A) | kWh | Metrology | float32 | R | 31209 | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | 41211 | [8 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 | 41212 | Imported Energy CH2 (B) | kWh | Metrology | float32 | R | 31211 | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | 41213 | [8 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 | 41214 | Imported Energy CH3 (C) | kWh | Metrology | float32 | R | 31213 | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | 41215 | [8 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 | 41216 | Exported VAh Sum Element | kVAh | Metrology | float32 | R | 31215 | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | 41217 | [8 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 | 41218 | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R | 31217 | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | 41219 | [8 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 | 41220 | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R | 31219 | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | 41221 | [8 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 | 41222 | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R | 31221 | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | 41223 | [8 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 | 41224 | Imported VAh Sum Element | kVAh | Metrology | float32 | R | 31223 | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | 41225 | [8 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 | 41226 | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R | 31225 | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | 41227 | [8 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 | 41228 | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R | 31227 | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | 41229 | [8 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 | 41230 | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R | 31229 | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | 41231 | [8 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 | 41232 | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R | 31231 | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | 41233 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 | 41234 | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R | 31233 | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | 41235 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 | 41236 | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R | 31235 | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | 41237 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 | 41238 | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R | 31237 | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | 41239 | [8 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 | 41240 | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R | 31239 | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | 41241 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 | 41242 | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R | 31241 | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | 41243 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 | 41244 | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R | 31243 | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | 41245 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 | 41246 | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R | 31245 | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | 41247 | [8 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 | 41248 | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R | 31247 | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | 41249 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 | 41250 | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R | 31249 | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | 41251 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 | 41252 | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R | 31251 | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | 41253 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 | 41254 | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R | 31253 | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | 41255 | [8 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 | 41256 | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R | 31255 | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | 41257 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 | 41258 | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R | 31257 | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | 41259 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 | 41260 | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R | 31259 | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | 41261 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 | 41262 | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R | 31261 | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | 41263 | [8 empty] | element |  |  | ALL
Events MSW | 1263 | 41264 | Events MSW |  |  | bitfield32 | R | 1263 | AI | Events | system |  |  | ALL
Events LSW | 1264 | 41265 | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 | 41266 | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 | 41267 | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
FACTORY REGISTERS | - | - | FACTORY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Factory Unlock Register | 2000 | 42001 | Factory Unlock Register |  | Factory | unit16 | R/W |  |  |  | system |  | Reserved | ALL
Factory Reset | 2001 | 42002 | Factory Reset |  | Factory | unit16 | R/W |  |  |  | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
OEM Vendor ID | 2002 | 42003 | OEM Vendor ID |  | Factory | unit16 | R |  |  |  | system |  | Reserved | ALL
FACTORY_CONFIG | 2003 | 42004 | Factory Config |  | Factory | unit16 | R |  |  |  | system | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable | ALL
USER COMMAND POINTS | - | - | USER COMMAND POINTS | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 | 42101 | Reset (software) processor |  | User | unit16 | W | 2100 | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 | 42102 | Clear all accumulated measurements (CAM) |  | User | unit16 | W | 2101 | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 | 42103 | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W | 32102 | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 | 42104 | Clear Peak Demand Element |  | User | unit16 | W | 32103 | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 | 42105 | Clear Peak Demand All |  | User | unit16 | W | 2104 | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 | 42106 | Reset to User Defaults |  | User | unit16 | W | 2105 | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - | USER CONFIG POINTS | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 | 42202 | Sliding or Fixed |  | Config | enum16 | R | 2201 | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 | 42203 | Demand Window | Min | Config | uint16 | R | 2202 | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 | 42204 | Volt Multiplier VINPUT1 |  | Config | float32 | R/W | 2203 | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | 42205 | [8 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 | 42206 | Volt Multiplier VINPUT2 |  | Config | float32 | R/W | 2205 | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | 42207 | [8 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 | 42208 | Service Type |  | Config | enum16 | R/W | 32207 | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 | 42209 | Snap MV Threshold | PER | Config | float32 | R/W | 2208 | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | 42210 | [8 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 | 42211 | Snap Rog Threshold | PER | Config | float32 | R/W | 2210 | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | 42212 | [8 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 | 42213 | Snap Volt Threshold | V | Config | float32 | R/W | 2212 | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | 42214 | [8 empty] | system |  |  | ALL
Communications Mode | 2214 | 42215 | Communications Mode |  | Config |  |  | 2214 | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 | 42216 | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W | 2215 | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | 42217 | [8 empty] | system |  |  | ALL
Voltage Input Element | 2217 | 42218 | Element Voltage Input |  | Config | enum16 | R/W | 32217 | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 | 42219 | CT1 RANGE | A | Config | float32 | R/W | 32218 | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | 42220 | [8 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 | 42221 | Voltage Reference for CT1 |  | Config | enum16 | R/W | 32220 | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 | 42222 | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W | 32221 | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | 42223 | [8 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 | 42224 | CT1 TYPE |  | Config | enum16 | R/W | 32223 | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 | 42225 | CT1 PHASE SHIFT | Deg | Config | float32 | R/W | 32224 | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | 42226 | [8 empty] | element |  |  | ALL
CH1 CT Sign | 2226 | 42227 | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W | 32226 | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 | 42228 | CT2 RANGE | A | Config | float32 | R/W | 32227 | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | 42229 | [8 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 | 42230 | Voltage Reference for CT2 |  | Config | enum16 | R/W | 32229 | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 | 42231 | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W | 32230 | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | 42232 | [8 empty] | element | >0 |  | ALL
CH2 CT type | 2232 | 42233 | CT2 TYPE |  | Config | enum16 | R/W | 32232 | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 | 42234 | CT2 PHASE SHIFT | Deg | Config | float32 | R/W | 32233 | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | 42235 | [8 empty] | element |  |  | ALL
CH2 CT Sign | 2235 | 42236 | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W | 32235 | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 | 42237 | CT3 INTEGER | A | Config | float32 | R/W | 32236 | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | 42238 | [8 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 | 42239 | Voltage Reference for CT3 |  | Config | enum16 | R/W | 32238 | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 | 42240 | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W | 32239 | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | 42241 | [8 empty] | element | >0 |  | ALL
CH3 CT type | 2241 | 42242 | CT3 TYPE |  | Config | enum16 | R/W | 32241 | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 | 42243 | CT3 PHASE SHIFT | Deg | Config | float32 | R/W | 32242 | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | 42244 | [8 empty] | element |  |  | ALL
CH3 CT Sign | 2244 | 42245 | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W | 32244 | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 | 42246 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 | 42247 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 | 42248 | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 | 42249 | PF Sign Convention |  | Config | uint16 | R/W | 2248 | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 | 42250 | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 | 42251 | BACnet UDP Port |  | Config | uint16 | R/W | 2250 | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 | 42252 | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 | 42253 | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | 42254 | [8 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 | 42261 | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | 42262 | [11 empty] | ALL
BACnet Max Info Frames | 2262 | 42263 | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 | 42264 | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 | 42265 | BBMD IP Address |  | Config | string(16) | R/W | 2264 | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | 42266 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | 42267 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | 42268 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | 42269 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | 42270 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | 42271 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | 42272 | [9 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 | 42273 | LCD/WebApp Read Password |  | Config | uint16 | R/W | 2272 | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 | 42274 | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 | 42275 | Customer Line frequency |  | Config | float | R/W | 2274 | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | 42276 | [10 empty] | Reserved | ALL
Communications Interface Configured | 2276 | 42277 | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 | 42278 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 | 42279 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 | 42280 | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 | 42281 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 | 42282 | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 | 42283 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 | 42284 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 | 42285 | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 | 42286 | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 | 42287 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 | 42288 | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 | 42289 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 | 42290 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 | 42291 | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 | 42292 | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | 42293 | [11 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 | 42294 | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | 42295 | [11 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 | 42296 | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 | 42297 | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - | METROLOGY POINTS | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 | 42301 | Displacement PF Avg Element | dPF | Metrology | float32 | R | 32300 | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | 42302 | [11 empty] | ALL
Displacement PF CH1 (MSW) | 2302 | 42303 | Displacement PF CH1 (A) | dPF | Metrology | float32 | R | 32302 | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | 42304 | [11 empty] | ALL
Displacement PF CH2 (MSW) | 2304 | 42305 | Displacement PF CH2 (B) | dPF | Metrology | float32 | R | 32304 | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | 42306 | [11 empty] | ALL
Displacement PF CH3 (MSW) | 2306 | 42307 | Displacement PF CH3 (C) | dPF | Metrology | float32 | R | 32306 | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | 42308 | [11 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 | 42309 | Avg Apparent PF Element | aPF | Metrology | float32 | R | 32308 | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | 42310 | [11 empty] | ALL
Apparent PF CH1 (MSW) | 2310 | 42311 | Apparent PF CH1 (A) | aPF | Metrology | float32 | R | 32310 | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | 42312 | [11 empty] | ALL
Apparent PF CH2 (MSW) | 2312 | 42313 | Apparent PF CH2 (B) | aPF | Metrology | float32 | R | 32312 | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | 42314 | [11 empty] | ALL
Apparent PF CH3 (MSW) | 2314 | 42315 | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R | 32314 | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | 42316 | [11 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 | 42317 | Distortion PF Avg Element | tPF | Metrology | float32 | R | 32316 | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | 42318 | [11 empty] | ALL
Distortion PF CH1 (MSW) | 2318 | 42319 | Distortion PF CH1 (A) | tPF | Metrology | float32 | R | 32318 | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | 42320 | [11 empty] | ALL
Distortion PF CH2 (MSW) | 2320 | 42321 | Distortion PF CH2 (B) | tPF | Metrology | float32 | R | 32320 | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | 42322 | [11 empty] | ALL
Distortion PF CH3 (MSW) | 2322 | 42323 | Distortion PF CH3 (C) | tPF | Metrology | float32 | R | 32322 | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | 42324 | [11 empty] | ALL
THD Avg Element (MSW) | 2324 | 42325 | THD Avg Element | % | Metrology | float32 | R | 32324 | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | 42326 | [11 empty] | ALL
THD CH1 (MSW) | 2326 | 42327 | THD CH1 (A) | % | Metrology | float32 | R | 32326 | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | 42328 | [11 empty] | ALL
THD CH2 (MSW) | 2328 | 42329 | THD CH2 (B) | % | Metrology | float32 | R | 32328 | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | 42330 | [11 empty] | ALL
THD CH3 (MSW) | 2330 | 42331 | THD CH3 (C) | % | Metrology | float32 | R | 32330 | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | 42332 | [11 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 | 42333 | Power Demand Max Interval Element | kW | Metrology | float32 | R | 32332 | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | 42334 | [11 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 | 42335 | Power Demand This Interval Element | kW | Metrology | float32 | R | 32334 | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | 42336 | [11 empty] | ALL
VA Peak Demand Element (MSW) | 2336 | 42337 | VA Demand Max Interval Element | kVA | Metrology | float32 | R | 32336 | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | 42338 | [11 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 | 42339 | VA Demand This Interval Element | kVA | Metrology | float32 | R | 32338 | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | 42340 | [11 empty] | ALL
Not Used | 2340 | 42341 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 | 42342 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 | 42343 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 | 42344 | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 | 42345 | Energy Net Sum Element | kWh | Metrology | float32 | R | 32344 | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | 42346 | [8 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 | 42347 | Energy Net CH1 | kWh | Metrology | float32 | R | 32346 | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | 42348 | [8 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 | 42349 | Energy Net CH2 | kWh | Metrology | float32 | R | 32348 | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | 42350 | [8 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 | 42351 | Energy Net CH3 | kWh | Metrology | float32 | R | 32350 | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | 42352 | [8 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 | 42353 | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R | 32352 | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | 42354 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 | 42355 | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R | 32354 | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | 42356 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 | 42357 | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R | 32356 | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | 42358 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 | 42359 | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R | 32358 | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | 42360 | [8 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 | 42361 | VARh Net Sum Element | kVArh | Metrology | float32 | R | 32360 | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | 42362 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 | 42363 | VARh Net CH1 | kVArh | Metrology | float32 | R | 32362 | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | 42364 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 | 42365 | VARh Net CH2 | kVArh | Metrology | float32 | R | 32364 | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | 42366 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 | 42367 | VARh Net CH3 | kVArh | Metrology | float32 | R | 32366 | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | 42368 | [8 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 | 42369 | Time Since Reset MSW | Sec | Metrology | uint32 |  | 2368 | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 | 42370 | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 | 42371 | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 | 42372 | CH1 Angle | Deg | Metrology | float32 | R | 32371 | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | 42373 | [8 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 | 42374 | CH2 Angle | Deg | Metrology | float32 | R | 32373 | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | 42375 | [8 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 | 42376 | CH3 Angle | Deg | Metrology | float32 | R | 32375 | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | 42377 | [11 empty] | ALL
Phase Chek System Status | 2377 | 42378 | System Phase Check Status |  | Metrology | bitfield16 | R | 2377 | BV | Phase Check System Status | system | 0,1 | 0 (All Channels OK), 1(Somewhere a channel is reading a dPF < 0.55), check register 2378 for each Element | ALL
Phase Chek Element Status | 2378 | 42379 | Element Phase Check Status |  | Metrology | bitfield16 | R | 32378 | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 | 42380 | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 | 42381 | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 | 42382 | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 | 42392 | Element Angle |  | Metrology | float | R | 32391 | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | 42393 | [11 empty] | ALL
PULSE INPUTS | - | - | PULSE INPUTS | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 | 42401 | Pulse Input 1 Enable |  | Config | uint16 | R/W | 2400 | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 | 42402 | Pulse Input 1 Scale Factor |  | Config | float32 | R/W | 2401 | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 | 42403 |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 | 42404 | Pulse Input 1 Units |  | Config | string(4) | R/W | 2403 | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 | 42405 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 | 42406 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 | 42407 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 | 42408 | Pulse Input 1 Accumulator |  | Metrology | float32 | R | 2407 | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | 42409 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 | 42410 | Pulse Input 1 Accumulator Clear |  | User | unit16 | W | 2409 | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 | 42411 | Pulse Input 2 Enable |  | Config | uint16 | R/W | 2410 | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 | 42412 | Pulse Input 2 Scale Factor |  | Config | float32 | R/W | 2411 | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | 42413 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 | 42414 | Pulse Input 2 Units |  | Config | string(4) | R/W | 2413 | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 | 42415 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 | 42416 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 | 42417 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 | 42418 | Pulse Input 2 Accumulator |  | Metrology | float32 | R | 2417 | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | 42419 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 | 42420 | Pulse Input 2 Accumulator Clear |  | User | unit16 | W | 2419 | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 | 42421 | Pulse Input 3 Enable |  | Config | uint16 | R/W | 2420 | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 | 42422 | Pulse Input 3 Scale Factor |  | Config | float32 | R/W | 2421 | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | 42423 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 | 42424 | Pulse Input 3 Units |  | Config | string(4) | R/W | 2423 | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 | 42425 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 | 42426 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 | 42427 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 | 42428 | Pulse Input 3 Accumulator |  | Metrology | float32 | R | 2427 | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | 42429 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 | 42430 | Pulse Input 3 Accumulator Clear |  | User |  | W | 2429 | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 | 42431 | Pulse Input 4 Enable |  | Config | uint16 | R/W | 2430 | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 | 42432 | Pulse Input 4 Scale Factor |  | Config | float32 | R/W | 2431 | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | 42433 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 | 42434 | Pulse Input 4 Units |  | Config | string(4) | R/W | 2433 | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 | 42435 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 | 42436 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 | 42437 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 | 42438 | Pulse Input 4 Accumulator |  | Metrology | float32 | R | 2437 | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | 42439 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 | 42440 | Pulse Input 4 Accumulator Clear |  | User | unit16 | W | 2439 | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - | ALARMS | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 | 42452 | State of Alarm |  | Metrology | uint16 | R/W | 2451 | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 | 42453 | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 | 42454 | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 | 42455 | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 | 42456 | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 | 42457 | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 | 42458 | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 | 42459 | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W | 2458 | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 | 42460 | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W | 2459 | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Range Vin1 L1N Under | 2460 | 42461 | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W | 2460 | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 | 42462 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2N Under | 2462 | 42463 | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W | 2462 | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 | 42464 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3N Under | 2464 | 42465 | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W | 2464 | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 | 42466 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L1L2 Under | 2466 | 42467 | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W | 2466 | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 | 42468 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2L3 Under | 2468 | 42469 | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W | 2468 | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 | 42470 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3L1 Under | 2470 | 42471 | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W | 2470 | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 | 42472 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin2 L1N Under | 2472 | 42473 | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W | 2472 | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 | 42474 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2N Under | 2474 | 42475 | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W | 2474 | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 | 42476 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3N Under | 2476 | 42477 | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W | 2476 | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 | 42478 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L1L2 Under | 2478 | 42479 | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W | 2478 | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 | 42480 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2L3 Under | 2480 | 42481 | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W | 2480 | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 | 42482 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3L1 Under | 2482 | 42483 | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W | 2482 | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 | 42484 | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 | 42485 | Voltage Alarm Persistence | Sec | Config | uint16 | R/W | 2484 | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 | 42486 | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R | 2485 | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 | 42487 | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 | 42488 | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R | 2487 | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 | 42489 | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 | 42490 | Real Time Clock MSW |  | Config | uint16 | R/W | 2489 | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 | 42491 | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - | USER CONFIG POINTS 2 | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 | 42602 | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 | 42603 | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 | 42604 | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 | 42605 | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 | 42606 | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 | 42607 | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 | 42608 | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 | 42609 | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 | 42610 | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 | 42611 | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 | 42612 | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 | 42613 | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 | 42614 | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 | 42615 | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 | 42616 | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 | 42617 | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 | 42618 | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 | 42619 | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 | 42620 | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 | 42621 | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 | 42622 | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 | 42623 | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 | 42624 | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 | 42625 | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 | 42626 | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 | 42627 | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 | 42628 | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 | 42629 | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 | 42630 | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 | 42631 | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 | 42632 | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 | 42633 | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 | 42634 | BACnet Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | 2634 | 42635 | BACnet Description 1 | [8 empty] | 2 Char |  | ALL
BACnet Description 2 | 2635 | 42636 | BACnet Description 2 | [8 empty] | 2 Char |  | ALL
BACnet Description 3 | 2636 | 42637 | BACnet Description 3 | [8 empty] | 2 Char |  | ALL
BACnet Description 4 | 2637 | 42638 | BACnet Description 4 | [8 empty] | 2 Char |  | ALL
BACnet Description 5 | 2638 | 42639 | BACnet Description 5 | [8 empty] | 2 Char |  | ALL
BACnet Description 6 | 2639 | 42640 | BACnet Description 6 | [8 empty] | 2 Char |  | ALL
BACnet Description 7 | 2640 | 42641 | BACnet Description 7 | [8 empty] | 2 Char |  | ALL
BACnet Description 8 | 2641 | 42642 | BACnet Description 8 | [8 empty] | 2 Char |  | ALL
BACnet Description 9 | 2642 | 42643 | BACnet Description 9 | [8 empty] | 2 Char |  | ALL
BACnet Description 10 | 2643 | 42644 | BACnet Description 10 | [8 empty] | 2 Char |  | ALL
BACnet Description 11 | 2644 | 42645 | BACnet Description 11 | [8 empty] | 2 Char |  | ALL
BACnet Description 12 | 2645 | 42646 | BACnet Description 12 | [8 empty] | 2 Char |  | ALL
BACnet Description 13 | 2646 | 42647 | BACnet Description 13 | [8 empty] | 2 Char |  | ALL
BACnet Description 14 | 2647 | 42648 | BACnet Description 14 | [8 empty] | 2 Char |  | ALL
BACnet Description 15 | 2648 | 42649 | BACnet Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
VERIS EMULATION LEGACY REGISTERS | - | - | VERIS EMULATION LEGACY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Veris Emulation Mode | 2200 | 42201 | Set to Veris Emulation Mode |  | Config | uint16 | R/W |  |  |  | system | 0-1 | 1 = Report Slave ID as Veris Model H8036 | ALL
kWh System LSW | 0 | 40001 | kWh System LSW | kWh | Veris | uint32 | R |  |  |  | element |  |  | ALL
kWh System MSW | 1 | 40002 | kWh System MSW | kWh | Veris |  | R |  |  |  | element |  |  | ALL
kW System | 2 | 40003 | kW System | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVAR System | 3 | 40004 | kVAR System | kVAR | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVA System | 4 | 40005 | kVA System | kVA | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF System | 5 | 40006 | Apparent PF System | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts Line to Line Avg | 6 | 40007 | Volts Line to Line Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts Line to Neutral Avg | 7 | 40008 | Volts Line to Neutral Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps System Avg | 8 | 40009 | Amps System Avg | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L1 | 9 | 40010 | kW L1 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L2 | 10 | 40011 | kW L2 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L3 | 11 | 40012 | kW L3 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L1 | 12 | 40013 | Apparent PF L1 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L2 | 13 | 40014 | Apparent PF L2 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L3 | 14 | 40015 | Apparent PF L3 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts L1 to L2 | 15 | 40016 | Volts L1 to L2 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to L3 | 16 | 40017 | Volts L2 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to L3 | 17 | 40018 | Volts L1 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to Neutral | 18 | 40019 | Volts L1 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to Neutral | 19 | 40020 | Volts L2 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L3 to Neutral | 20 | 40021 | Volts L3 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps L1 | 21 | 40022 | Amps L1 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L2 | 22 | 40023 | Amps L2 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L3 | 23 | 40024 | Amps L3 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW System Avg | 24 | 40025 | kW System Avg | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Now | 25 | 40026 | kW Demand Sys Now (was Min) | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Max | 26 | 40027 | kW Demand Sys Max | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL

## E
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS --> | 5
BACNET OBJECT FLOOR --> | 40000
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 | 41002 | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | 41003 | [8 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 | 41004 | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 | 41005 | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 | 41006 | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | 41007 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | 41008 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | 41009 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | 41010 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | 41011 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | 41012 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | 41013 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | 41014 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | 41015 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | 41016 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | 41017 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | 41018 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | 41019 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | 41020 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | 41021 | [8 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 | 41022 | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | 41023 | [8 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | 41024 | [8 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | 41025 | [8 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | 41026 | [8 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | 41027 | [8 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | 41028 | [8 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | 41029 | [8 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | 41030 | [8 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | 41031 | [8 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | 41032 | [8 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | 41033 | [8 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | 41034 | [8 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | 41035 | [8 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | 41036 | [8 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | 41037 | [8 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 | 41038 | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | 41039 | [8 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | 41040 | [8 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | 41041 | [8 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | 41042 | [8 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | 41043 | [8 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | 41044 | [8 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | 41045 | [8 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 | 41046 | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | 41047 | [8 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | 41048 | [8 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | 41049 | [8 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | 41050 | [8 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | 41051 | [8 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | 41052 | [8 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | 41053 | [8 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 | 41054 | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | 41055 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | 41056 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | 41057 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | 41058 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | 41059 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | 41060 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | 41061 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | 41062 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | 41063 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | 41064 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | 41065 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | 41066 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | 41067 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | 41068 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | 41069 | [8 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 | 41070 | Modbus Device Address |  |  | unit16 | R/W | 1069 | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | 41071 | [8 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 | 41072 | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 | 41073 | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 | 41074 | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | 41075 | [8 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | 41076 | [8 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | 41077 | [8 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 | 41078 | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 | 41079 | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 | 41080 | IP Address |  |  | string(8) | R/W | 1079 | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | 41081 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | 41082 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | 41083 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | 41084 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | 41085 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | 41086 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | 41087 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 | 41088 | Netmask |  |  | string(8) | R/W | 1087 | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | 41089 | [8 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | 41090 | [8 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | 41091 | [8 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | 41092 | [8 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | 41093 | [8 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | 41094 | [8 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | 41095 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 | 41096 | Gateway |  |  | string(8) | R/W | 1095 | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | 41097 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | 41098 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | 41099 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | 41100 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | 41101 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | 41102 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | 41103 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 | 41104 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | 41105 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | 41106 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | 41107 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | 41108 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | 41109 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | 41110 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | 41111 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 | 41112 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | 41113 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | 41114 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | 41115 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | 41116 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | 41117 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | 41118 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | 41119 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 | 41120 | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | 41121 | [8 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | 41122 | [8 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | 41123 | [8 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 | 41124 | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | 41125 | [9 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 | 41126 | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 | 41127 | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 | 41128 | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | 41129 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | 41130 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | 41131 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 | 41132 | Interface baud rate in bits per second |  |  | uint32 | R/W | 1131 | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | 41133 | [8 empty] | system |  |  | ALL
SERIAL BITS | 1133 | 41134 | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 | 41135 | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 | 41136 | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 | 41137 | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 | 41138 | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 | 41139 | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 | 41140 | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 | 41141 | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 | 41142 | Current Avg Element | A | Metrology | float32 | R | 41141 | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | 41143 | [8 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 | 41144 | Current CH1 (A) | A | Metrology | float32 | R | 41143 | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | 41145 | [8 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 | 41146 | Current CH2 (B) | A | Metrology | float32 | R | 41145 | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | 41147 | [8 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 | 41148 | Current CH3 (C) | A | Metrology | float32 | R | 41147 | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | 41149 | [8 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 | 41150 | Voltage L to N Avg Element | V | Metrology | float32 | R | 41149 | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | 41151 | [8 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 | 41152 | Voltage L1 to N (AN) | V | Metrology | float32 | R | 41151 | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | 41153 | [8 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 | 41154 | Voltage L2 to N (BN) | V | Metrology | float32 | R | 41153 | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | 41155 | [8 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 | 41156 | Voltage L3 to N (CN) | V | Metrology | float32 | R | 41155 | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | 41157 | [8 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 | 41158 | Voltage L to L Avg Element | V | Metrology | float32 | R | 41157 | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | 41159 | [8 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 | 41160 | Voltage L1 to L2 (AB) | V | Metrology | float32 | R | 41159 | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | 41161 | [8 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 | 41162 | Voltage L2 to L3 (BC) | V | Metrology | float32 | R | 41161 | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | 41163 | [8 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 | 41164 | Voltage L3 to L1 (CA) | V | Metrology | float32 | R | 41163 | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | 41165 | [8 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 | 41166 | Line Frequency | Hz | Metrology | float32 | R | 41165 | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | 41167 | [8 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 | 41168 | Power Sum Element | kW | Metrology | float32 | R | 41167 | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | 41169 | [8 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 | 41170 | Power CH1 (A) | kW | Metrology | float32 | R | 41169 | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | 41171 | [8 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 | 41172 | Power CH2 (B) | kW | Metrology | float32 | R | 41171 | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | 41173 | [8 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 | 41174 | Power CH3 (C) | kW | Metrology | float32 | R | 41173 | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | 41175 | [8 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 | 41176 | VA Sum Element | kVA | Metrology | float32 | R | 41175 | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | 41177 | [8 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 | 41178 | VA CH1 (A) | kVA | Metrology | float32 | R | 41177 | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | 41179 | [8 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 | 41180 | VA CH2 (B) | kVA | Metrology | float32 | R | 41179 | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | 41181 | [8 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 | 41182 | VA CH3 (C) | kVA | Metrology | float32 | R | 41181 | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | 41183 | [8 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 | 41184 | VAR Sum Element | kVAr | Metrology | float32 | R | 41183 | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | 41185 | [8 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 | 41186 | VAR CH1 (A) | kVAr | Metrology | float32 | R | 41185 | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | 41187 | [8 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 | 41188 | VAR CH2 (B) | kVAr | Metrology | float32 | R | 41187 | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | 41189 | [8 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 | 41190 | VAR CH3 (C) | kVAr | Metrology | float32 | R | 41189 | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | 41191 | [8 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 | 41192 | Apparent PF Avg Element | PF | Metrology | float32 | R | 41191 | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | 41193 | [8 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 | 41194 | Apparent PF CH1 (A) | PF | Metrology | float32 | R | 41193 | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | 41195 | [8 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 | 41196 | Apparent PF CH2 (B) | PF | Metrology | float32 | R | 41195 | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | 41197 | [8 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 | 41198 | Apparent PF CH3 ( C) | PF | Metrology | float32 | R | 41197 | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | 41199 | [8 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 | 41200 | Exported Energy Sum Element | kWh | Metrology | float32 | R | 41199 | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | 41201 | [8 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 | 41202 | Exported Energy CH1 (A) | kWh | Metrology | float32 | R | 41201 | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | 41203 | [8 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 | 41204 | Exported Energy CH2 (B) | kWh | Metrology | float32 | R | 41203 | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | 41205 | [8 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 | 41206 | Exported Energy CH3 (C) | kWh | Metrology | float32 | R | 41205 | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | 41207 | [8 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 | 41208 | Imported Energy Sum Element | kWh | Metrology | float32 | R | 41207 | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | 41209 | [8 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 | 41210 | Imported Energy CH1 (A) | kWh | Metrology | float32 | R | 41209 | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | 41211 | [8 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 | 41212 | Imported Energy CH2 (B) | kWh | Metrology | float32 | R | 41211 | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | 41213 | [8 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 | 41214 | Imported Energy CH3 (C) | kWh | Metrology | float32 | R | 41213 | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | 41215 | [8 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 | 41216 | Exported VAh Sum Element | kVAh | Metrology | float32 | R | 41215 | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | 41217 | [8 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 | 41218 | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R | 41217 | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | 41219 | [8 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 | 41220 | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R | 41219 | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | 41221 | [8 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 | 41222 | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R | 41221 | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | 41223 | [8 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 | 41224 | Imported VAh Sum Element | kVAh | Metrology | float32 | R | 41223 | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | 41225 | [8 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 | 41226 | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R | 41225 | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | 41227 | [8 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 | 41228 | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R | 41227 | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | 41229 | [8 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 | 41230 | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R | 41229 | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | 41231 | [8 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 | 41232 | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R | 41231 | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | 41233 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 | 41234 | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R | 41233 | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | 41235 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 | 41236 | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R | 41235 | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | 41237 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 | 41238 | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R | 41237 | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | 41239 | [8 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 | 41240 | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R | 41239 | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | 41241 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 | 41242 | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R | 41241 | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | 41243 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 | 41244 | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R | 41243 | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | 41245 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 | 41246 | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R | 41245 | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | 41247 | [8 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 | 41248 | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R | 41247 | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | 41249 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 | 41250 | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R | 41249 | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | 41251 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 | 41252 | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R | 41251 | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | 41253 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 | 41254 | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R | 41253 | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | 41255 | [8 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 | 41256 | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R | 41255 | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | 41257 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 | 41258 | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R | 41257 | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | 41259 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 | 41260 | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R | 41259 | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | 41261 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 | 41262 | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R | 41261 | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | 41263 | [8 empty] | element |  |  | ALL
Events MSW | 1263 | 41264 | Events MSW |  |  | bitfield32 | R | 1263 | AI | Events | system |  |  | ALL
Events LSW | 1264 | 41265 | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 | 41266 | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 | 41267 | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
FACTORY REGISTERS | - | - | FACTORY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Factory Unlock Register | 2000 | 42001 | Factory Unlock Register |  | Factory | unit16 | R/W |  |  |  | system |  | Reserved | ALL
Factory Reset | 2001 | 42002 | Factory Reset |  | Factory | unit16 | R/W |  |  |  | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
OEM Vendor ID | 2002 | 42003 | OEM Vendor ID |  | Factory | unit16 | R |  |  |  | system |  | Reserved | ALL
FACTORY_CONFIG | 2003 | 42004 | Factory Config |  | Factory | unit16 | R |  |  |  | system | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable | ALL
USER COMMAND POINTS | - | - | USER COMMAND POINTS | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 | 42101 | Reset (software) processor |  | User | unit16 | W | 2100 | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 | 42102 | Clear all accumulated measurements (CAM) |  | User | unit16 | W | 2101 | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 | 42103 | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W | 42102 | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 | 42104 | Clear Peak Demand Element |  | User | unit16 | W | 42103 | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 | 42105 | Clear Peak Demand All |  | User | unit16 | W | 2104 | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 | 42106 | Reset to User Defaults |  | User | unit16 | W | 2105 | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - | USER CONFIG POINTS | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 | 42202 | Sliding or Fixed |  | Config | enum16 | R | 2201 | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 | 42203 | Demand Window | Min | Config | uint16 | R | 2202 | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 | 42204 | Volt Multiplier VINPUT1 |  | Config | float32 | R/W | 2203 | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | 42205 | [8 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 | 42206 | Volt Multiplier VINPUT2 |  | Config | float32 | R/W | 2205 | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | 42207 | [8 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 | 42208 | Service Type |  | Config | enum16 | R/W | 42207 | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 | 42209 | Snap MV Threshold | PER | Config | float32 | R/W | 2208 | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | 42210 | [8 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 | 42211 | Snap Rog Threshold | PER | Config | float32 | R/W | 2210 | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | 42212 | [8 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 | 42213 | Snap Volt Threshold | V | Config | float32 | R/W | 2212 | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | 42214 | [8 empty] | system |  |  | ALL
Communications Mode | 2214 | 42215 | Communications Mode |  | Config |  |  | 2214 | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 | 42216 | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W | 2215 | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | 42217 | [8 empty] | system |  |  | ALL
Voltage Input Element | 2217 | 42218 | Element Voltage Input |  | Config | enum16 | R/W | 42217 | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 | 42219 | CT1 RANGE | A | Config | float32 | R/W | 42218 | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | 42220 | [8 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 | 42221 | Voltage Reference for CT1 |  | Config | enum16 | R/W | 42220 | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 | 42222 | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W | 42221 | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | 42223 | [8 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 | 42224 | CT1 TYPE |  | Config | enum16 | R/W | 42223 | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 | 42225 | CT1 PHASE SHIFT | Deg | Config | float32 | R/W | 42224 | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | 42226 | [8 empty] | element |  |  | ALL
CH1 CT Sign | 2226 | 42227 | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W | 42226 | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 | 42228 | CT2 RANGE | A | Config | float32 | R/W | 42227 | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | 42229 | [8 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 | 42230 | Voltage Reference for CT2 |  | Config | enum16 | R/W | 42229 | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 | 42231 | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W | 42230 | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | 42232 | [8 empty] | element | >0 |  | ALL
CH2 CT type | 2232 | 42233 | CT2 TYPE |  | Config | enum16 | R/W | 42232 | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 | 42234 | CT2 PHASE SHIFT | Deg | Config | float32 | R/W | 42233 | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | 42235 | [8 empty] | element |  |  | ALL
CH2 CT Sign | 2235 | 42236 | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W | 42235 | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 | 42237 | CT3 INTEGER | A | Config | float32 | R/W | 42236 | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | 42238 | [8 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 | 42239 | Voltage Reference for CT3 |  | Config | enum16 | R/W | 42238 | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 | 42240 | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W | 42239 | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | 42241 | [8 empty] | element | >0 |  | ALL
CH3 CT type | 2241 | 42242 | CT3 TYPE |  | Config | enum16 | R/W | 42241 | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 | 42243 | CT3 PHASE SHIFT | Deg | Config | float32 | R/W | 42242 | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | 42244 | [8 empty] | element |  |  | ALL
CH3 CT Sign | 2244 | 42245 | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W | 42244 | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 | 42246 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 | 42247 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 | 42248 | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 | 42249 | PF Sign Convention |  | Config | uint16 | R/W | 2248 | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 | 42250 | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 | 42251 | BACnet UDP Port |  | Config | uint16 | R/W | 2250 | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 | 42252 | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 | 42253 | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | 42254 | [8 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 | 42261 | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | 42262 | [11 empty] | ALL
BACnet Max Info Frames | 2262 | 42263 | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 | 42264 | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 | 42265 | BBMD IP Address |  | Config | string(16) | R/W | 2264 | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | 42266 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | 42267 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | 42268 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | 42269 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | 42270 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | 42271 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | 42272 | [9 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 | 42273 | LCD/WebApp Read Password |  | Config | uint16 | R/W | 2272 | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 | 42274 | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 | 42275 | Customer Line frequency |  | Config | float | R/W | 2274 | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | 42276 | [10 empty] | Reserved | ALL
Communications Interface Configured | 2276 | 42277 | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 | 42278 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 | 42279 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 | 42280 | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 | 42281 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 | 42282 | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 | 42283 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 | 42284 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 | 42285 | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 | 42286 | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 | 42287 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 | 42288 | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 | 42289 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 | 42290 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 | 42291 | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 | 42292 | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | 42293 | [11 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 | 42294 | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | 42295 | [11 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 | 42296 | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 | 42297 | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - | METROLOGY POINTS | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 | 42301 | Displacement PF Avg Element | dPF | Metrology | float32 | R | 42300 | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | 42302 | [11 empty] | ALL
Displacement PF CH1 (MSW) | 2302 | 42303 | Displacement PF CH1 (A) | dPF | Metrology | float32 | R | 42302 | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | 42304 | [11 empty] | ALL
Displacement PF CH2 (MSW) | 2304 | 42305 | Displacement PF CH2 (B) | dPF | Metrology | float32 | R | 42304 | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | 42306 | [11 empty] | ALL
Displacement PF CH3 (MSW) | 2306 | 42307 | Displacement PF CH3 (C) | dPF | Metrology | float32 | R | 42306 | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | 42308 | [11 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 | 42309 | Avg Apparent PF Element | aPF | Metrology | float32 | R | 42308 | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | 42310 | [11 empty] | ALL
Apparent PF CH1 (MSW) | 2310 | 42311 | Apparent PF CH1 (A) | aPF | Metrology | float32 | R | 42310 | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | 42312 | [11 empty] | ALL
Apparent PF CH2 (MSW) | 2312 | 42313 | Apparent PF CH2 (B) | aPF | Metrology | float32 | R | 42312 | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | 42314 | [11 empty] | ALL
Apparent PF CH3 (MSW) | 2314 | 42315 | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R | 42314 | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | 42316 | [11 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 | 42317 | Distortion PF Avg Element | tPF | Metrology | float32 | R | 42316 | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | 42318 | [11 empty] | ALL
Distortion PF CH1 (MSW) | 2318 | 42319 | Distortion PF CH1 (A) | tPF | Metrology | float32 | R | 42318 | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | 42320 | [11 empty] | ALL
Distortion PF CH2 (MSW) | 2320 | 42321 | Distortion PF CH2 (B) | tPF | Metrology | float32 | R | 42320 | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | 42322 | [11 empty] | ALL
Distortion PF CH3 (MSW) | 2322 | 42323 | Distortion PF CH3 (C) | tPF | Metrology | float32 | R | 42322 | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | 42324 | [11 empty] | ALL
THD Avg Element (MSW) | 2324 | 42325 | THD Avg Element | % | Metrology | float32 | R | 42324 | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | 42326 | [11 empty] | ALL
THD CH1 (MSW) | 2326 | 42327 | THD CH1 (A) | % | Metrology | float32 | R | 42326 | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | 42328 | [11 empty] | ALL
THD CH2 (MSW) | 2328 | 42329 | THD CH2 (B) | % | Metrology | float32 | R | 42328 | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | 42330 | [11 empty] | ALL
THD CH3 (MSW) | 2330 | 42331 | THD CH3 (C) | % | Metrology | float32 | R | 42330 | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | 42332 | [11 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 | 42333 | Power Demand Max Interval Element | kW | Metrology | float32 | R | 42332 | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | 42334 | [11 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 | 42335 | Power Demand This Interval Element | kW | Metrology | float32 | R | 42334 | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | 42336 | [11 empty] | ALL
VA Peak Demand Element (MSW) | 2336 | 42337 | VA Demand Max Interval Element | kVA | Metrology | float32 | R | 42336 | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | 42338 | [11 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 | 42339 | VA Demand This Interval Element | kVA | Metrology | float32 | R | 42338 | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | 42340 | [11 empty] | ALL
Not Used | 2340 | 42341 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 | 42342 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 | 42343 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 | 42344 | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 | 42345 | Energy Net Sum Element | kWh | Metrology | float32 | R | 42344 | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | 42346 | [8 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 | 42347 | Energy Net CH1 | kWh | Metrology | float32 | R | 42346 | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | 42348 | [8 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 | 42349 | Energy Net CH2 | kWh | Metrology | float32 | R | 42348 | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | 42350 | [8 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 | 42351 | Energy Net CH3 | kWh | Metrology | float32 | R | 42350 | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | 42352 | [8 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 | 42353 | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R | 42352 | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | 42354 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 | 42355 | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R | 42354 | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | 42356 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 | 42357 | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R | 42356 | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | 42358 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 | 42359 | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R | 42358 | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | 42360 | [8 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 | 42361 | VARh Net Sum Element | kVArh | Metrology | float32 | R | 42360 | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | 42362 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 | 42363 | VARh Net CH1 | kVArh | Metrology | float32 | R | 42362 | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | 42364 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 | 42365 | VARh Net CH2 | kVArh | Metrology | float32 | R | 42364 | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | 42366 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 | 42367 | VARh Net CH3 | kVArh | Metrology | float32 | R | 42366 | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | 42368 | [8 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 | 42369 | Time Since Reset MSW | Sec | Metrology | uint32 |  | 2368 | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 | 42370 | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 | 42371 | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 | 42372 | CH1 Angle | Deg | Metrology | float32 | R | 42371 | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | 42373 | [8 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 | 42374 | CH2 Angle | Deg | Metrology | float32 | R | 42373 | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | 42375 | [8 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 | 42376 | CH3 Angle | Deg | Metrology | float32 | R | 42375 | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | 42377 | [11 empty] | ALL
Phase Chek System Status | 2377 | 42378 | System Phase Check Status |  | Metrology | bitfield16 | R | 2377 | BV | Phase Check System Status | system | 0,1 | 0 (All Channels OK), 1(Somewhere a channel is reading a dPF < 0.55), check register 2378 for each Element | ALL
Phase Chek Element Status | 2378 | 42379 | Element Phase Check Status |  | Metrology | bitfield16 | R | 42378 | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 | 42380 | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 | 42381 | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 | 42382 | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 | 42392 | Element Angle |  | Metrology | float | R | 42391 | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | 42393 | [11 empty] | ALL
PULSE INPUTS | - | - | PULSE INPUTS | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 | 42401 | Pulse Input 1 Enable |  | Config | uint16 | R/W | 2400 | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 | 42402 | Pulse Input 1 Scale Factor |  | Config | float32 | R/W | 2401 | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 | 42403 |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 | 42404 | Pulse Input 1 Units |  | Config | string(4) | R/W | 2403 | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 | 42405 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 | 42406 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 | 42407 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 | 42408 | Pulse Input 1 Accumulator |  | Metrology | float32 | R | 2407 | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | 42409 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 | 42410 | Pulse Input 1 Accumulator Clear |  | User | unit16 | W | 2409 | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 | 42411 | Pulse Input 2 Enable |  | Config | uint16 | R/W | 2410 | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 | 42412 | Pulse Input 2 Scale Factor |  | Config | float32 | R/W | 2411 | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | 42413 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 | 42414 | Pulse Input 2 Units |  | Config | string(4) | R/W | 2413 | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 | 42415 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 | 42416 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 | 42417 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 | 42418 | Pulse Input 2 Accumulator |  | Metrology | float32 | R | 2417 | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | 42419 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 | 42420 | Pulse Input 2 Accumulator Clear |  | User | unit16 | W | 2419 | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 | 42421 | Pulse Input 3 Enable |  | Config | uint16 | R/W | 2420 | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 | 42422 | Pulse Input 3 Scale Factor |  | Config | float32 | R/W | 2421 | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | 42423 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 | 42424 | Pulse Input 3 Units |  | Config | string(4) | R/W | 2423 | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 | 42425 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 | 42426 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 | 42427 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 | 42428 | Pulse Input 3 Accumulator |  | Metrology | float32 | R | 2427 | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | 42429 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 | 42430 | Pulse Input 3 Accumulator Clear |  | User |  | W | 2429 | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 | 42431 | Pulse Input 4 Enable |  | Config | uint16 | R/W | 2430 | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 | 42432 | Pulse Input 4 Scale Factor |  | Config | float32 | R/W | 2431 | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | 42433 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 | 42434 | Pulse Input 4 Units |  | Config | string(4) | R/W | 2433 | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 | 42435 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 | 42436 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 | 42437 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 | 42438 | Pulse Input 4 Accumulator |  | Metrology | float32 | R | 2437 | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | 42439 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 | 42440 | Pulse Input 4 Accumulator Clear |  | User | unit16 | W | 2439 | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - | ALARMS | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 | 42452 | State of Alarm |  | Metrology | uint16 | R/W | 2451 | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 | 42453 | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 | 42454 | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 | 42455 | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 | 42456 | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 | 42457 | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 | 42458 | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 | 42459 | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W | 2458 | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 | 42460 | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W | 2459 | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Range Vin1 L1N Under | 2460 | 42461 | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W | 2460 | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 | 42462 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2N Under | 2462 | 42463 | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W | 2462 | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 | 42464 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3N Under | 2464 | 42465 | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W | 2464 | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 | 42466 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L1L2 Under | 2466 | 42467 | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W | 2466 | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 | 42468 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2L3 Under | 2468 | 42469 | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W | 2468 | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 | 42470 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3L1 Under | 2470 | 42471 | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W | 2470 | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 | 42472 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin2 L1N Under | 2472 | 42473 | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W | 2472 | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 | 42474 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2N Under | 2474 | 42475 | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W | 2474 | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 | 42476 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3N Under | 2476 | 42477 | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W | 2476 | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 | 42478 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L1L2 Under | 2478 | 42479 | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W | 2478 | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 | 42480 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2L3 Under | 2480 | 42481 | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W | 2480 | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 | 42482 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3L1 Under | 2482 | 42483 | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W | 2482 | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 | 42484 | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 | 42485 | Voltage Alarm Persistence | Sec | Config | uint16 | R/W | 2484 | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 | 42486 | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R | 2485 | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 | 42487 | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 | 42488 | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R | 2487 | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 | 42489 | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 | 42490 | Real Time Clock MSW |  | Config | uint16 | R/W | 2489 | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 | 42491 | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - | USER CONFIG POINTS 2 | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 | 42602 | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 | 42603 | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 | 42604 | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 | 42605 | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 | 42606 | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 | 42607 | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 | 42608 | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 | 42609 | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 | 42610 | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 | 42611 | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 | 42612 | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 | 42613 | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 | 42614 | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 | 42615 | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 | 42616 | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 | 42617 | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 | 42618 | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 | 42619 | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 | 42620 | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 | 42621 | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 | 42622 | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 | 42623 | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 | 42624 | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 | 42625 | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 | 42626 | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 | 42627 | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 | 42628 | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 | 42629 | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 | 42630 | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 | 42631 | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 | 42632 | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 | 42633 | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 | 42634 | BACnet Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | 2634 | 42635 | BACnet Description 1 | [8 empty] | 2 Char |  | ALL
BACnet Description 2 | 2635 | 42636 | BACnet Description 2 | [8 empty] | 2 Char |  | ALL
BACnet Description 3 | 2636 | 42637 | BACnet Description 3 | [8 empty] | 2 Char |  | ALL
BACnet Description 4 | 2637 | 42638 | BACnet Description 4 | [8 empty] | 2 Char |  | ALL
BACnet Description 5 | 2638 | 42639 | BACnet Description 5 | [8 empty] | 2 Char |  | ALL
BACnet Description 6 | 2639 | 42640 | BACnet Description 6 | [8 empty] | 2 Char |  | ALL
BACnet Description 7 | 2640 | 42641 | BACnet Description 7 | [8 empty] | 2 Char |  | ALL
BACnet Description 8 | 2641 | 42642 | BACnet Description 8 | [8 empty] | 2 Char |  | ALL
BACnet Description 9 | 2642 | 42643 | BACnet Description 9 | [8 empty] | 2 Char |  | ALL
BACnet Description 10 | 2643 | 42644 | BACnet Description 10 | [8 empty] | 2 Char |  | ALL
BACnet Description 11 | 2644 | 42645 | BACnet Description 11 | [8 empty] | 2 Char |  | ALL
BACnet Description 12 | 2645 | 42646 | BACnet Description 12 | [8 empty] | 2 Char |  | ALL
BACnet Description 13 | 2646 | 42647 | BACnet Description 13 | [8 empty] | 2 Char |  | ALL
BACnet Description 14 | 2647 | 42648 | BACnet Description 14 | [8 empty] | 2 Char |  | ALL
BACnet Description 15 | 2648 | 42649 | BACnet Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
VERIS EMULATION LEGACY REGISTERS | - | - | VERIS EMULATION LEGACY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Veris Emulation Mode | 2200 | 42201 | Set to Veris Emulation Mode |  | Config | uint16 | R/W |  |  |  | system | 0-1 | 1 = Report Slave ID as Veris Model H8036 | ALL
kWh System LSW | 0 | 40001 | kWh System LSW | kWh | Veris | uint32 | R |  |  |  | element |  |  | ALL
kWh System MSW | 1 | 40002 | kWh System MSW | kWh | Veris |  | R |  |  |  | element |  |  | ALL
kW System | 2 | 40003 | kW System | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVAR System | 3 | 40004 | kVAR System | kVAR | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVA System | 4 | 40005 | kVA System | kVA | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF System | 5 | 40006 | Apparent PF System | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts Line to Line Avg | 6 | 40007 | Volts Line to Line Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts Line to Neutral Avg | 7 | 40008 | Volts Line to Neutral Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps System Avg | 8 | 40009 | Amps System Avg | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L1 | 9 | 40010 | kW L1 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L2 | 10 | 40011 | kW L2 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L3 | 11 | 40012 | kW L3 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L1 | 12 | 40013 | Apparent PF L1 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L2 | 13 | 40014 | Apparent PF L2 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L3 | 14 | 40015 | Apparent PF L3 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts L1 to L2 | 15 | 40016 | Volts L1 to L2 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to L3 | 16 | 40017 | Volts L2 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to L3 | 17 | 40018 | Volts L1 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to Neutral | 18 | 40019 | Volts L1 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to Neutral | 19 | 40020 | Volts L2 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L3 to Neutral | 20 | 40021 | Volts L3 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps L1 | 21 | 40022 | Amps L1 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L2 | 22 | 40023 | Amps L2 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L3 | 23 | 40024 | Amps L3 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW System Avg | 24 | 40025 | kW System Avg | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Now | 25 | 40026 | kW Demand Sys Now (was Min) | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Max | 26 | 40027 | kW Demand Sys Max | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL

## F
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS --> | 6
BACNET OBJECT FLOOR --> | 50000
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 | 41002 | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | 41003 | [8 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 | 41004 | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 | 41005 | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 | 41006 | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | 41007 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | 41008 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | 41009 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | 41010 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | 41011 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | 41012 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | 41013 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | 41014 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | 41015 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | 41016 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | 41017 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | 41018 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | 41019 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | 41020 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | 41021 | [8 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 | 41022 | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | 41023 | [8 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | 41024 | [8 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | 41025 | [8 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | 41026 | [8 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | 41027 | [8 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | 41028 | [8 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | 41029 | [8 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | 41030 | [8 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | 41031 | [8 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | 41032 | [8 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | 41033 | [8 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | 41034 | [8 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | 41035 | [8 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | 41036 | [8 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | 41037 | [8 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 | 41038 | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | 41039 | [8 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | 41040 | [8 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | 41041 | [8 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | 41042 | [8 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | 41043 | [8 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | 41044 | [8 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | 41045 | [8 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 | 41046 | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | 41047 | [8 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | 41048 | [8 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | 41049 | [8 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | 41050 | [8 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | 41051 | [8 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | 41052 | [8 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | 41053 | [8 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 | 41054 | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | 41055 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | 41056 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | 41057 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | 41058 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | 41059 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | 41060 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | 41061 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | 41062 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | 41063 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | 41064 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | 41065 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | 41066 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | 41067 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | 41068 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | 41069 | [8 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 | 41070 | Modbus Device Address |  |  | unit16 | R/W | 1069 | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | 41071 | [8 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 | 41072 | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 | 41073 | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 | 41074 | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | 41075 | [8 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | 41076 | [8 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | 41077 | [8 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 | 41078 | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 | 41079 | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 | 41080 | IP Address |  |  | string(8) | R/W | 1079 | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | 41081 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | 41082 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | 41083 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | 41084 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | 41085 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | 41086 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | 41087 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 | 41088 | Netmask |  |  | string(8) | R/W | 1087 | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | 41089 | [8 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | 41090 | [8 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | 41091 | [8 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | 41092 | [8 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | 41093 | [8 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | 41094 | [8 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | 41095 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 | 41096 | Gateway |  |  | string(8) | R/W | 1095 | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | 41097 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | 41098 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | 41099 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | 41100 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | 41101 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | 41102 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | 41103 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 | 41104 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | 41105 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | 41106 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | 41107 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | 41108 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | 41109 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | 41110 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | 41111 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 | 41112 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | 41113 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | 41114 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | 41115 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | 41116 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | 41117 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | 41118 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | 41119 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 | 41120 | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | 41121 | [8 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | 41122 | [8 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | 41123 | [8 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 | 41124 | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | 41125 | [9 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 | 41126 | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 | 41127 | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 | 41128 | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | 41129 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | 41130 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | 41131 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 | 41132 | Interface baud rate in bits per second |  |  | uint32 | R/W | 1131 | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | 41133 | [8 empty] | system |  |  | ALL
SERIAL BITS | 1133 | 41134 | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 | 41135 | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 | 41136 | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 | 41137 | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 | 41138 | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 | 41139 | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 | 41140 | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 | 41141 | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 | 41142 | Current Avg Element | A | Metrology | float32 | R | 51141 | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | 41143 | [8 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 | 41144 | Current CH1 (A) | A | Metrology | float32 | R | 51143 | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | 41145 | [8 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 | 41146 | Current CH2 (B) | A | Metrology | float32 | R | 51145 | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | 41147 | [8 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 | 41148 | Current CH3 (C) | A | Metrology | float32 | R | 51147 | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | 41149 | [8 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 | 41150 | Voltage L to N Avg Element | V | Metrology | float32 | R | 51149 | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | 41151 | [8 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 | 41152 | Voltage L1 to N (AN) | V | Metrology | float32 | R | 51151 | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | 41153 | [8 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 | 41154 | Voltage L2 to N (BN) | V | Metrology | float32 | R | 51153 | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | 41155 | [8 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 | 41156 | Voltage L3 to N (CN) | V | Metrology | float32 | R | 51155 | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | 41157 | [8 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 | 41158 | Voltage L to L Avg Element | V | Metrology | float32 | R | 51157 | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | 41159 | [8 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 | 41160 | Voltage L1 to L2 (AB) | V | Metrology | float32 | R | 51159 | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | 41161 | [8 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 | 41162 | Voltage L2 to L3 (BC) | V | Metrology | float32 | R | 51161 | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | 41163 | [8 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 | 41164 | Voltage L3 to L1 (CA) | V | Metrology | float32 | R | 51163 | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | 41165 | [8 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 | 41166 | Line Frequency | Hz | Metrology | float32 | R | 51165 | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | 41167 | [8 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 | 41168 | Power Sum Element | kW | Metrology | float32 | R | 51167 | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | 41169 | [8 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 | 41170 | Power CH1 (A) | kW | Metrology | float32 | R | 51169 | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | 41171 | [8 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 | 41172 | Power CH2 (B) | kW | Metrology | float32 | R | 51171 | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | 41173 | [8 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 | 41174 | Power CH3 (C) | kW | Metrology | float32 | R | 51173 | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | 41175 | [8 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 | 41176 | VA Sum Element | kVA | Metrology | float32 | R | 51175 | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | 41177 | [8 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 | 41178 | VA CH1 (A) | kVA | Metrology | float32 | R | 51177 | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | 41179 | [8 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 | 41180 | VA CH2 (B) | kVA | Metrology | float32 | R | 51179 | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | 41181 | [8 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 | 41182 | VA CH3 (C) | kVA | Metrology | float32 | R | 51181 | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | 41183 | [8 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 | 41184 | VAR Sum Element | kVAr | Metrology | float32 | R | 51183 | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | 41185 | [8 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 | 41186 | VAR CH1 (A) | kVAr | Metrology | float32 | R | 51185 | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | 41187 | [8 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 | 41188 | VAR CH2 (B) | kVAr | Metrology | float32 | R | 51187 | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | 41189 | [8 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 | 41190 | VAR CH3 (C) | kVAr | Metrology | float32 | R | 51189 | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | 41191 | [8 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 | 41192 | Apparent PF Avg Element | PF | Metrology | float32 | R | 51191 | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | 41193 | [8 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 | 41194 | Apparent PF CH1 (A) | PF | Metrology | float32 | R | 51193 | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | 41195 | [8 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 | 41196 | Apparent PF CH2 (B) | PF | Metrology | float32 | R | 51195 | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | 41197 | [8 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 | 41198 | Apparent PF CH3 ( C) | PF | Metrology | float32 | R | 51197 | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | 41199 | [8 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 | 41200 | Exported Energy Sum Element | kWh | Metrology | float32 | R | 51199 | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | 41201 | [8 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 | 41202 | Exported Energy CH1 (A) | kWh | Metrology | float32 | R | 51201 | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | 41203 | [8 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 | 41204 | Exported Energy CH2 (B) | kWh | Metrology | float32 | R | 51203 | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | 41205 | [8 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 | 41206 | Exported Energy CH3 (C) | kWh | Metrology | float32 | R | 51205 | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | 41207 | [8 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 | 41208 | Imported Energy Sum Element | kWh | Metrology | float32 | R | 51207 | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | 41209 | [8 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 | 41210 | Imported Energy CH1 (A) | kWh | Metrology | float32 | R | 51209 | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | 41211 | [8 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 | 41212 | Imported Energy CH2 (B) | kWh | Metrology | float32 | R | 51211 | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | 41213 | [8 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 | 41214 | Imported Energy CH3 (C) | kWh | Metrology | float32 | R | 51213 | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | 41215 | [8 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 | 41216 | Exported VAh Sum Element | kVAh | Metrology | float32 | R | 51215 | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | 41217 | [8 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 | 41218 | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R | 51217 | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | 41219 | [8 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 | 41220 | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R | 51219 | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | 41221 | [8 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 | 41222 | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R | 51221 | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | 41223 | [8 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 | 41224 | Imported VAh Sum Element | kVAh | Metrology | float32 | R | 51223 | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | 41225 | [8 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 | 41226 | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R | 51225 | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | 41227 | [8 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 | 41228 | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R | 51227 | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | 41229 | [8 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 | 41230 | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R | 51229 | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | 41231 | [8 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 | 41232 | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R | 51231 | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | 41233 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 | 41234 | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R | 51233 | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | 41235 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 | 41236 | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R | 51235 | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | 41237 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 | 41238 | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R | 51237 | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | 41239 | [8 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 | 41240 | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R | 51239 | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | 41241 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 | 41242 | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R | 51241 | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | 41243 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 | 41244 | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R | 51243 | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | 41245 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 | 41246 | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R | 51245 | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | 41247 | [8 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 | 41248 | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R | 51247 | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | 41249 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 | 41250 | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R | 51249 | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | 41251 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 | 41252 | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R | 51251 | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | 41253 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 | 41254 | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R | 51253 | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | 41255 | [8 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 | 41256 | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R | 51255 | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | 41257 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 | 41258 | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R | 51257 | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | 41259 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 | 41260 | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R | 51259 | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | 41261 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 | 41262 | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R | 51261 | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | 41263 | [8 empty] | element |  |  | ALL
Events MSW | 1263 | 41264 | Events MSW |  |  | bitfield32 | R | 1263 | AI | Events | system |  |  | ALL
Events LSW | 1264 | 41265 | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 | 41266 | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 | 41267 | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
FACTORY REGISTERS | - | - | FACTORY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Factory Unlock Register | 2000 | 42001 | Factory Unlock Register |  | Factory | unit16 | R/W |  |  |  | system |  | Reserved | ALL
Factory Reset | 2001 | 42002 | Factory Reset |  | Factory | unit16 | R/W |  |  |  | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
OEM Vendor ID | 2002 | 42003 | OEM Vendor ID |  | Factory | unit16 | R |  |  |  | system |  | Reserved | ALL
FACTORY_CONFIG | 2003 | 42004 | Factory Config |  | Factory | unit16 | R |  |  |  | system | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable | ALL
USER COMMAND POINTS | - | - | USER COMMAND POINTS | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 | 42101 | Reset (software) processor |  | User | unit16 | W | 2100 | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 | 42102 | Clear all accumulated measurements (CAM) |  | User | unit16 | W | 2101 | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 | 42103 | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W | 52102 | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 | 42104 | Clear Peak Demand Element |  | User | unit16 | W | 52103 | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 | 42105 | Clear Peak Demand All |  | User | unit16 | W | 2104 | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 | 42106 | Reset to User Defaults |  | User | unit16 | W | 2105 | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - | USER CONFIG POINTS | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 | 42202 | Sliding or Fixed |  | Config | enum16 | R | 2201 | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 | 42203 | Demand Window | Min | Config | uint16 | R | 2202 | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 | 42204 | Volt Multiplier VINPUT1 |  | Config | float32 | R/W | 2203 | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | 42205 | [8 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 | 42206 | Volt Multiplier VINPUT2 |  | Config | float32 | R/W | 2205 | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | 42207 | [8 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 | 42208 | Service Type |  | Config | enum16 | R/W | 52207 | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 | 42209 | Snap MV Threshold | PER | Config | float32 | R/W | 2208 | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | 42210 | [8 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 | 42211 | Snap Rog Threshold | PER | Config | float32 | R/W | 2210 | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | 42212 | [8 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 | 42213 | Snap Volt Threshold | V | Config | float32 | R/W | 2212 | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | 42214 | [8 empty] | system |  |  | ALL
Communications Mode | 2214 | 42215 | Communications Mode |  | Config |  |  | 2214 | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 | 42216 | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W | 2215 | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | 42217 | [8 empty] | system |  |  | ALL
Voltage Input Element | 2217 | 42218 | Element Voltage Input |  | Config | enum16 | R/W | 52217 | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 | 42219 | CT1 RANGE | A | Config | float32 | R/W | 52218 | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | 42220 | [8 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 | 42221 | Voltage Reference for CT1 |  | Config | enum16 | R/W | 52220 | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 | 42222 | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W | 52221 | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | 42223 | [8 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 | 42224 | CT1 TYPE |  | Config | enum16 | R/W | 52223 | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 | 42225 | CT1 PHASE SHIFT | Deg | Config | float32 | R/W | 52224 | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | 42226 | [8 empty] | element |  |  | ALL
CH1 CT Sign | 2226 | 42227 | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W | 52226 | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 | 42228 | CT2 RANGE | A | Config | float32 | R/W | 52227 | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | 42229 | [8 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 | 42230 | Voltage Reference for CT2 |  | Config | enum16 | R/W | 52229 | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 | 42231 | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W | 52230 | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | 42232 | [8 empty] | element | >0 |  | ALL
CH2 CT type | 2232 | 42233 | CT2 TYPE |  | Config | enum16 | R/W | 52232 | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 | 42234 | CT2 PHASE SHIFT | Deg | Config | float32 | R/W | 52233 | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | 42235 | [8 empty] | element |  |  | ALL
CH2 CT Sign | 2235 | 42236 | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W | 52235 | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 | 42237 | CT3 INTEGER | A | Config | float32 | R/W | 52236 | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | 42238 | [8 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 | 42239 | Voltage Reference for CT3 |  | Config | enum16 | R/W | 52238 | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 | 42240 | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W | 52239 | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | 42241 | [8 empty] | element | >0 |  | ALL
CH3 CT type | 2241 | 42242 | CT3 TYPE |  | Config | enum16 | R/W | 52241 | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 | 42243 | CT3 PHASE SHIFT | Deg | Config | float32 | R/W | 52242 | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | 42244 | [8 empty] | element |  |  | ALL
CH3 CT Sign | 2244 | 42245 | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W | 52244 | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 | 42246 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 | 42247 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 | 42248 | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 | 42249 | PF Sign Convention |  | Config | uint16 | R/W | 2248 | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 | 42250 | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 | 42251 | BACnet UDP Port |  | Config | uint16 | R/W | 2250 | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 | 42252 | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 | 42253 | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | 42254 | [8 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 | 42261 | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | 42262 | [11 empty] | ALL
BACnet Max Info Frames | 2262 | 42263 | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 | 42264 | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 | 42265 | BBMD IP Address |  | Config | string(16) | R/W | 2264 | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | 42266 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | 42267 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | 42268 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | 42269 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | 42270 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | 42271 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | 42272 | [9 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 | 42273 | LCD/WebApp Read Password |  | Config | uint16 | R/W | 2272 | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 | 42274 | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 | 42275 | Customer Line frequency |  | Config | float | R/W | 2274 | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | 42276 | [10 empty] | Reserved | ALL
Communications Interface Configured | 2276 | 42277 | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 | 42278 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 | 42279 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 | 42280 | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 | 42281 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 | 42282 | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 | 42283 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 | 42284 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 | 42285 | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 | 42286 | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 | 42287 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 | 42288 | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 | 42289 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 | 42290 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 | 42291 | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 | 42292 | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | 42293 | [11 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 | 42294 | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | 42295 | [11 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 | 42296 | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 | 42297 | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - | METROLOGY POINTS | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 | 42301 | Displacement PF Avg Element | dPF | Metrology | float32 | R | 52300 | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | 42302 | [11 empty] | ALL
Displacement PF CH1 (MSW) | 2302 | 42303 | Displacement PF CH1 (A) | dPF | Metrology | float32 | R | 52302 | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | 42304 | [11 empty] | ALL
Displacement PF CH2 (MSW) | 2304 | 42305 | Displacement PF CH2 (B) | dPF | Metrology | float32 | R | 52304 | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | 42306 | [11 empty] | ALL
Displacement PF CH3 (MSW) | 2306 | 42307 | Displacement PF CH3 (C) | dPF | Metrology | float32 | R | 52306 | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | 42308 | [11 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 | 42309 | Avg Apparent PF Element | aPF | Metrology | float32 | R | 52308 | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | 42310 | [11 empty] | ALL
Apparent PF CH1 (MSW) | 2310 | 42311 | Apparent PF CH1 (A) | aPF | Metrology | float32 | R | 52310 | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | 42312 | [11 empty] | ALL
Apparent PF CH2 (MSW) | 2312 | 42313 | Apparent PF CH2 (B) | aPF | Metrology | float32 | R | 52312 | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | 42314 | [11 empty] | ALL
Apparent PF CH3 (MSW) | 2314 | 42315 | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R | 52314 | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | 42316 | [11 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 | 42317 | Distortion PF Avg Element | tPF | Metrology | float32 | R | 52316 | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | 42318 | [11 empty] | ALL
Distortion PF CH1 (MSW) | 2318 | 42319 | Distortion PF CH1 (A) | tPF | Metrology | float32 | R | 52318 | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | 42320 | [11 empty] | ALL
Distortion PF CH2 (MSW) | 2320 | 42321 | Distortion PF CH2 (B) | tPF | Metrology | float32 | R | 52320 | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | 42322 | [11 empty] | ALL
Distortion PF CH3 (MSW) | 2322 | 42323 | Distortion PF CH3 (C) | tPF | Metrology | float32 | R | 52322 | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | 42324 | [11 empty] | ALL
THD Avg Element (MSW) | 2324 | 42325 | THD Avg Element | % | Metrology | float32 | R | 52324 | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | 42326 | [11 empty] | ALL
THD CH1 (MSW) | 2326 | 42327 | THD CH1 (A) | % | Metrology | float32 | R | 52326 | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | 42328 | [11 empty] | ALL
THD CH2 (MSW) | 2328 | 42329 | THD CH2 (B) | % | Metrology | float32 | R | 52328 | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | 42330 | [11 empty] | ALL
THD CH3 (MSW) | 2330 | 42331 | THD CH3 (C) | % | Metrology | float32 | R | 52330 | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | 42332 | [11 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 | 42333 | Power Demand Max Interval Element | kW | Metrology | float32 | R | 52332 | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | 42334 | [11 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 | 42335 | Power Demand This Interval Element | kW | Metrology | float32 | R | 52334 | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | 42336 | [11 empty] | ALL
VA Peak Demand Element (MSW) | 2336 | 42337 | VA Demand Max Interval Element | kVA | Metrology | float32 | R | 52336 | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | 42338 | [11 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 | 42339 | VA Demand This Interval Element | kVA | Metrology | float32 | R | 52338 | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | 42340 | [11 empty] | ALL
Not Used | 2340 | 42341 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 | 42342 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 | 42343 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 | 42344 | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 | 42345 | Energy Net Sum Element | kWh | Metrology | float32 | R | 52344 | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | 42346 | [8 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 | 42347 | Energy Net CH1 | kWh | Metrology | float32 | R | 52346 | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | 42348 | [8 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 | 42349 | Energy Net CH2 | kWh | Metrology | float32 | R | 52348 | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | 42350 | [8 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 | 42351 | Energy Net CH3 | kWh | Metrology | float32 | R | 52350 | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | 42352 | [8 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 | 42353 | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R | 52352 | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | 42354 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 | 42355 | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R | 52354 | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | 42356 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 | 42357 | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R | 52356 | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | 42358 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 | 42359 | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R | 52358 | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | 42360 | [8 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 | 42361 | VARh Net Sum Element | kVArh | Metrology | float32 | R | 52360 | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | 42362 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 | 42363 | VARh Net CH1 | kVArh | Metrology | float32 | R | 52362 | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | 42364 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 | 42365 | VARh Net CH2 | kVArh | Metrology | float32 | R | 52364 | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | 42366 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 | 42367 | VARh Net CH3 | kVArh | Metrology | float32 | R | 52366 | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | 42368 | [8 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 | 42369 | Time Since Reset MSW | Sec | Metrology | uint32 |  | 2368 | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 | 42370 | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 | 42371 | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 | 42372 | CH1 Angle | Deg | Metrology | float32 | R | 52371 | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | 42373 | [8 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 | 42374 | CH2 Angle | Deg | Metrology | float32 | R | 52373 | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | 42375 | [8 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 | 42376 | CH3 Angle | Deg | Metrology | float32 | R | 52375 | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | 42377 | [11 empty] | ALL
Phase Chek System Status | 2377 | 42378 | System Phase Check Status |  | Metrology | bitfield16 | R | 2377 | BV | Phase Check System Status | system | 0,1 | 0 (All Channels OK), 1(Somewhere a channel is reading a dPF < 0.55), check register 2378 for each Element | ALL
Phase Chek Element Status | 2378 | 42379 | Element Phase Check Status |  | Metrology | bitfield16 | R | 52378 | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 | 42380 | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 | 42381 | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 | 42382 | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 | 42392 | Element Angle |  | Metrology | float | R | 52391 | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | 42393 | [11 empty] | ALL
PULSE INPUTS | - | - | PULSE INPUTS | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 | 42401 | Pulse Input 1 Enable |  | Config | uint16 | R/W | 2400 | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 | 42402 | Pulse Input 1 Scale Factor |  | Config | float32 | R/W | 2401 | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 | 42403 |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 | 42404 | Pulse Input 1 Units |  | Config | string(4) | R/W | 2403 | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 | 42405 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 | 42406 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 | 42407 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 | 42408 | Pulse Input 1 Accumulator |  | Metrology | float32 | R | 2407 | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | 42409 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 | 42410 | Pulse Input 1 Accumulator Clear |  | User | unit16 | W | 2409 | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 | 42411 | Pulse Input 2 Enable |  | Config | uint16 | R/W | 2410 | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 | 42412 | Pulse Input 2 Scale Factor |  | Config | float32 | R/W | 2411 | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | 42413 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 | 42414 | Pulse Input 2 Units |  | Config | string(4) | R/W | 2413 | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 | 42415 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 | 42416 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 | 42417 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 | 42418 | Pulse Input 2 Accumulator |  | Metrology | float32 | R | 2417 | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | 42419 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 | 42420 | Pulse Input 2 Accumulator Clear |  | User | unit16 | W | 2419 | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 | 42421 | Pulse Input 3 Enable |  | Config | uint16 | R/W | 2420 | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 | 42422 | Pulse Input 3 Scale Factor |  | Config | float32 | R/W | 2421 | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | 42423 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 | 42424 | Pulse Input 3 Units |  | Config | string(4) | R/W | 2423 | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 | 42425 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 | 42426 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 | 42427 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 | 42428 | Pulse Input 3 Accumulator |  | Metrology | float32 | R | 2427 | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | 42429 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 | 42430 | Pulse Input 3 Accumulator Clear |  | User |  | W | 2429 | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 | 42431 | Pulse Input 4 Enable |  | Config | uint16 | R/W | 2430 | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 | 42432 | Pulse Input 4 Scale Factor |  | Config | float32 | R/W | 2431 | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | 42433 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 | 42434 | Pulse Input 4 Units |  | Config | string(4) | R/W | 2433 | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 | 42435 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 | 42436 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 | 42437 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 | 42438 | Pulse Input 4 Accumulator |  | Metrology | float32 | R | 2437 | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | 42439 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 | 42440 | Pulse Input 4 Accumulator Clear |  | User | unit16 | W | 2439 | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - | ALARMS | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 | 42452 | State of Alarm |  | Metrology | uint16 | R/W | 2451 | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 | 42453 | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 | 42454 | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 | 42455 | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 | 42456 | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 | 42457 | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 | 42458 | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 | 42459 | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W | 2458 | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 | 42460 | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W | 2459 | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Range Vin1 L1N Under | 2460 | 42461 | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W | 2460 | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 | 42462 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2N Under | 2462 | 42463 | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W | 2462 | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 | 42464 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3N Under | 2464 | 42465 | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W | 2464 | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 | 42466 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L1L2 Under | 2466 | 42467 | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W | 2466 | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 | 42468 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2L3 Under | 2468 | 42469 | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W | 2468 | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 | 42470 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3L1 Under | 2470 | 42471 | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W | 2470 | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 | 42472 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin2 L1N Under | 2472 | 42473 | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W | 2472 | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 | 42474 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2N Under | 2474 | 42475 | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W | 2474 | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 | 42476 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3N Under | 2476 | 42477 | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W | 2476 | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 | 42478 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L1L2 Under | 2478 | 42479 | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W | 2478 | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 | 42480 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2L3 Under | 2480 | 42481 | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W | 2480 | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 | 42482 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3L1 Under | 2482 | 42483 | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W | 2482 | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 | 42484 | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 | 42485 | Voltage Alarm Persistence | Sec | Config | uint16 | R/W | 2484 | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 | 42486 | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R | 2485 | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 | 42487 | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 | 42488 | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R | 2487 | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 | 42489 | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 | 42490 | Real Time Clock MSW |  | Config | uint16 | R/W | 2489 | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 | 42491 | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - | USER CONFIG POINTS 2 | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 | 42602 | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 | 42603 | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 | 42604 | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 | 42605 | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 | 42606 | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 | 42607 | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 | 42608 | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 | 42609 | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 | 42610 | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 | 42611 | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 | 42612 | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 | 42613 | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 | 42614 | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 | 42615 | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 | 42616 | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 | 42617 | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 | 42618 | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 | 42619 | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 | 42620 | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 | 42621 | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 | 42622 | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 | 42623 | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 | 42624 | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 | 42625 | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 | 42626 | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 | 42627 | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 | 42628 | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 | 42629 | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 | 42630 | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 | 42631 | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 | 42632 | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 | 42633 | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 | 42634 | BACnet Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | 2634 | 42635 | BACnet Description 1 | [8 empty] | 2 Char |  | ALL
BACnet Description 2 | 2635 | 42636 | BACnet Description 2 | [8 empty] | 2 Char |  | ALL
BACnet Description 3 | 2636 | 42637 | BACnet Description 3 | [8 empty] | 2 Char |  | ALL
BACnet Description 4 | 2637 | 42638 | BACnet Description 4 | [8 empty] | 2 Char |  | ALL
BACnet Description 5 | 2638 | 42639 | BACnet Description 5 | [8 empty] | 2 Char |  | ALL
BACnet Description 6 | 2639 | 42640 | BACnet Description 6 | [8 empty] | 2 Char |  | ALL
BACnet Description 7 | 2640 | 42641 | BACnet Description 7 | [8 empty] | 2 Char |  | ALL
BACnet Description 8 | 2641 | 42642 | BACnet Description 8 | [8 empty] | 2 Char |  | ALL
BACnet Description 9 | 2642 | 42643 | BACnet Description 9 | [8 empty] | 2 Char |  | ALL
BACnet Description 10 | 2643 | 42644 | BACnet Description 10 | [8 empty] | 2 Char |  | ALL
BACnet Description 11 | 2644 | 42645 | BACnet Description 11 | [8 empty] | 2 Char |  | ALL
BACnet Description 12 | 2645 | 42646 | BACnet Description 12 | [8 empty] | 2 Char |  | ALL
BACnet Description 13 | 2646 | 42647 | BACnet Description 13 | [8 empty] | 2 Char |  | ALL
BACnet Description 14 | 2647 | 42648 | BACnet Description 14 | [8 empty] | 2 Char |  | ALL
BACnet Description 15 | 2648 | 42649 | BACnet Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
VERIS EMULATION LEGACY REGISTERS | - | - | VERIS EMULATION LEGACY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Veris Emulation Mode | 2200 | 42201 | Set to Veris Emulation Mode |  | Config | uint16 | R/W |  |  |  | system | 0-1 | 1 = Report Slave ID as Veris Model H8036 | ALL
kWh System LSW | 0 | 40001 | kWh System LSW | kWh | Veris | uint32 | R |  |  |  | element |  |  | ALL
kWh System MSW | 1 | 40002 | kWh System MSW | kWh | Veris |  | R |  |  |  | element |  |  | ALL
kW System | 2 | 40003 | kW System | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVAR System | 3 | 40004 | kVAR System | kVAR | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVA System | 4 | 40005 | kVA System | kVA | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF System | 5 | 40006 | Apparent PF System | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts Line to Line Avg | 6 | 40007 | Volts Line to Line Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts Line to Neutral Avg | 7 | 40008 | Volts Line to Neutral Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps System Avg | 8 | 40009 | Amps System Avg | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L1 | 9 | 40010 | kW L1 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L2 | 10 | 40011 | kW L2 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L3 | 11 | 40012 | kW L3 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L1 | 12 | 40013 | Apparent PF L1 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L2 | 13 | 40014 | Apparent PF L2 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L3 | 14 | 40015 | Apparent PF L3 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts L1 to L2 | 15 | 40016 | Volts L1 to L2 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to L3 | 16 | 40017 | Volts L2 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to L3 | 17 | 40018 | Volts L1 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to Neutral | 18 | 40019 | Volts L1 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to Neutral | 19 | 40020 | Volts L2 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L3 to Neutral | 20 | 40021 | Volts L3 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps L1 | 21 | 40022 | Amps L1 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L2 | 22 | 40023 | Amps L2 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L3 | 23 | 40024 | Amps L3 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW System Avg | 24 | 40025 | kW System Avg | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Now | 25 | 40026 | kW Demand Sys Now (was Min) | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Max | 26 | 40027 | kW Demand Sys Max | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL

## G
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS --> | 7
BACNET OBJECT FLOOR --> | 60000
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 | 41002 | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | 41003 | [8 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 | 41004 | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 | 41005 | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 | 41006 | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | 41007 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | 41008 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | 41009 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | 41010 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | 41011 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | 41012 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | 41013 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | 41014 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | 41015 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | 41016 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | 41017 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | 41018 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | 41019 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | 41020 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | 41021 | [8 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 | 41022 | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | 41023 | [8 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | 41024 | [8 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | 41025 | [8 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | 41026 | [8 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | 41027 | [8 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | 41028 | [8 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | 41029 | [8 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | 41030 | [8 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | 41031 | [8 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | 41032 | [8 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | 41033 | [8 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | 41034 | [8 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | 41035 | [8 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | 41036 | [8 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | 41037 | [8 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 | 41038 | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | 41039 | [8 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | 41040 | [8 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | 41041 | [8 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | 41042 | [8 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | 41043 | [8 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | 41044 | [8 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | 41045 | [8 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 | 41046 | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | 41047 | [8 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | 41048 | [8 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | 41049 | [8 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | 41050 | [8 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | 41051 | [8 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | 41052 | [8 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | 41053 | [8 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 | 41054 | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | 41055 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | 41056 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | 41057 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | 41058 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | 41059 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | 41060 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | 41061 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | 41062 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | 41063 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | 41064 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | 41065 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | 41066 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | 41067 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | 41068 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | 41069 | [8 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 | 41070 | Modbus Device Address |  |  | unit16 | R/W | 1069 | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | 41071 | [8 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 | 41072 | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 | 41073 | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 | 41074 | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | 41075 | [8 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | 41076 | [8 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | 41077 | [8 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 | 41078 | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 | 41079 | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 | 41080 | IP Address |  |  | string(8) | R/W | 1079 | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | 41081 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | 41082 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | 41083 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | 41084 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | 41085 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | 41086 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | 41087 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 | 41088 | Netmask |  |  | string(8) | R/W | 1087 | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | 41089 | [8 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | 41090 | [8 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | 41091 | [8 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | 41092 | [8 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | 41093 | [8 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | 41094 | [8 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | 41095 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 | 41096 | Gateway |  |  | string(8) | R/W | 1095 | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | 41097 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | 41098 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | 41099 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | 41100 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | 41101 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | 41102 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | 41103 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 | 41104 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | 41105 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | 41106 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | 41107 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | 41108 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | 41109 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | 41110 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | 41111 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 | 41112 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | 41113 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | 41114 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | 41115 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | 41116 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | 41117 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | 41118 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | 41119 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 | 41120 | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | 41121 | [8 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | 41122 | [8 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | 41123 | [8 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 | 41124 | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | 41125 | [9 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 | 41126 | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 | 41127 | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 | 41128 | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | 41129 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | 41130 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | 41131 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 | 41132 | Interface baud rate in bits per second |  |  | uint32 | R/W | 1131 | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | 41133 | [8 empty] | system |  |  | ALL
SERIAL BITS | 1133 | 41134 | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 | 41135 | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 | 41136 | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 | 41137 | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 | 41138 | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 | 41139 | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 | 41140 | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 | 41141 | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 | 41142 | Current Avg Element | A | Metrology | float32 | R | 61141 | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | 41143 | [8 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 | 41144 | Current CH1 (A) | A | Metrology | float32 | R | 61143 | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | 41145 | [8 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 | 41146 | Current CH2 (B) | A | Metrology | float32 | R | 61145 | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | 41147 | [8 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 | 41148 | Current CH3 (C) | A | Metrology | float32 | R | 61147 | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | 41149 | [8 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 | 41150 | Voltage L to N Avg Element | V | Metrology | float32 | R | 61149 | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | 41151 | [8 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 | 41152 | Voltage L1 to N (AN) | V | Metrology | float32 | R | 61151 | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | 41153 | [8 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 | 41154 | Voltage L2 to N (BN) | V | Metrology | float32 | R | 61153 | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | 41155 | [8 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 | 41156 | Voltage L3 to N (CN) | V | Metrology | float32 | R | 61155 | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | 41157 | [8 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 | 41158 | Voltage L to L Avg Element | V | Metrology | float32 | R | 61157 | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | 41159 | [8 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 | 41160 | Voltage L1 to L2 (AB) | V | Metrology | float32 | R | 61159 | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | 41161 | [8 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 | 41162 | Voltage L2 to L3 (BC) | V | Metrology | float32 | R | 61161 | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | 41163 | [8 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 | 41164 | Voltage L3 to L1 (CA) | V | Metrology | float32 | R | 61163 | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | 41165 | [8 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 | 41166 | Line Frequency | Hz | Metrology | float32 | R | 61165 | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | 41167 | [8 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 | 41168 | Power Sum Element | kW | Metrology | float32 | R | 61167 | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | 41169 | [8 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 | 41170 | Power CH1 (A) | kW | Metrology | float32 | R | 61169 | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | 41171 | [8 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 | 41172 | Power CH2 (B) | kW | Metrology | float32 | R | 61171 | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | 41173 | [8 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 | 41174 | Power CH3 (C) | kW | Metrology | float32 | R | 61173 | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | 41175 | [8 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 | 41176 | VA Sum Element | kVA | Metrology | float32 | R | 61175 | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | 41177 | [8 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 | 41178 | VA CH1 (A) | kVA | Metrology | float32 | R | 61177 | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | 41179 | [8 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 | 41180 | VA CH2 (B) | kVA | Metrology | float32 | R | 61179 | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | 41181 | [8 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 | 41182 | VA CH3 (C) | kVA | Metrology | float32 | R | 61181 | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | 41183 | [8 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 | 41184 | VAR Sum Element | kVAr | Metrology | float32 | R | 61183 | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | 41185 | [8 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 | 41186 | VAR CH1 (A) | kVAr | Metrology | float32 | R | 61185 | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | 41187 | [8 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 | 41188 | VAR CH2 (B) | kVAr | Metrology | float32 | R | 61187 | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | 41189 | [8 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 | 41190 | VAR CH3 (C) | kVAr | Metrology | float32 | R | 61189 | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | 41191 | [8 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 | 41192 | Apparent PF Avg Element | PF | Metrology | float32 | R | 61191 | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | 41193 | [8 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 | 41194 | Apparent PF CH1 (A) | PF | Metrology | float32 | R | 61193 | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | 41195 | [8 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 | 41196 | Apparent PF CH2 (B) | PF | Metrology | float32 | R | 61195 | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | 41197 | [8 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 | 41198 | Apparent PF CH3 ( C) | PF | Metrology | float32 | R | 61197 | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | 41199 | [8 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 | 41200 | Exported Energy Sum Element | kWh | Metrology | float32 | R | 61199 | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | 41201 | [8 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 | 41202 | Exported Energy CH1 (A) | kWh | Metrology | float32 | R | 61201 | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | 41203 | [8 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 | 41204 | Exported Energy CH2 (B) | kWh | Metrology | float32 | R | 61203 | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | 41205 | [8 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 | 41206 | Exported Energy CH3 (C) | kWh | Metrology | float32 | R | 61205 | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | 41207 | [8 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 | 41208 | Imported Energy Sum Element | kWh | Metrology | float32 | R | 61207 | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | 41209 | [8 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 | 41210 | Imported Energy CH1 (A) | kWh | Metrology | float32 | R | 61209 | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | 41211 | [8 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 | 41212 | Imported Energy CH2 (B) | kWh | Metrology | float32 | R | 61211 | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | 41213 | [8 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 | 41214 | Imported Energy CH3 (C) | kWh | Metrology | float32 | R | 61213 | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | 41215 | [8 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 | 41216 | Exported VAh Sum Element | kVAh | Metrology | float32 | R | 61215 | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | 41217 | [8 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 | 41218 | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R | 61217 | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | 41219 | [8 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 | 41220 | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R | 61219 | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | 41221 | [8 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 | 41222 | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R | 61221 | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | 41223 | [8 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 | 41224 | Imported VAh Sum Element | kVAh | Metrology | float32 | R | 61223 | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | 41225 | [8 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 | 41226 | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R | 61225 | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | 41227 | [8 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 | 41228 | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R | 61227 | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | 41229 | [8 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 | 41230 | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R | 61229 | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | 41231 | [8 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 | 41232 | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R | 61231 | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | 41233 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 | 41234 | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R | 61233 | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | 41235 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 | 41236 | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R | 61235 | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | 41237 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 | 41238 | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R | 61237 | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | 41239 | [8 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 | 41240 | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R | 61239 | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | 41241 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 | 41242 | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R | 61241 | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | 41243 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 | 41244 | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R | 61243 | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | 41245 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 | 41246 | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R | 61245 | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | 41247 | [8 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 | 41248 | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R | 61247 | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | 41249 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 | 41250 | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R | 61249 | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | 41251 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 | 41252 | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R | 61251 | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | 41253 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 | 41254 | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R | 61253 | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | 41255 | [8 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 | 41256 | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R | 61255 | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | 41257 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 | 41258 | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R | 61257 | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | 41259 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 | 41260 | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R | 61259 | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | 41261 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 | 41262 | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R | 61261 | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | 41263 | [8 empty] | element |  |  | ALL
Events MSW | 1263 | 41264 | Events MSW |  |  | bitfield32 | R | 1263 | AI | Events | system |  |  | ALL
Events LSW | 1264 | 41265 | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 | 41266 | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 | 41267 | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
FACTORY REGISTERS | - | - | FACTORY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Factory Unlock Register | 2000 | 42001 | Factory Unlock Register |  | Factory | unit16 | R/W |  |  |  | system |  | Reserved | ALL
Factory Reset | 2001 | 42002 | Factory Reset |  | Factory | unit16 | R/W |  |  |  | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
OEM Vendor ID | 2002 | 42003 | OEM Vendor ID |  | Factory | unit16 | R |  |  |  | system |  | Reserved | ALL
FACTORY_CONFIG | 2003 | 42004 | Factory Config |  | Factory | unit16 | R |  |  |  | system | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable | ALL
USER COMMAND POINTS | - | - | USER COMMAND POINTS | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 | 42101 | Reset (software) processor |  | User | unit16 | W | 2100 | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 | 42102 | Clear all accumulated measurements (CAM) |  | User | unit16 | W | 2101 | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 | 42103 | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W | 62102 | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 | 42104 | Clear Peak Demand Element |  | User | unit16 | W | 62103 | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 | 42105 | Clear Peak Demand All |  | User | unit16 | W | 2104 | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 | 42106 | Reset to User Defaults |  | User | unit16 | W | 2105 | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - | USER CONFIG POINTS | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 | 42202 | Sliding or Fixed |  | Config | enum16 | R | 2201 | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 | 42203 | Demand Window | Min | Config | uint16 | R | 2202 | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 | 42204 | Volt Multiplier VINPUT1 |  | Config | float32 | R/W | 2203 | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | 42205 | [8 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 | 42206 | Volt Multiplier VINPUT2 |  | Config | float32 | R/W | 2205 | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | 42207 | [8 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 | 42208 | Service Type |  | Config | enum16 | R/W | 62207 | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 | 42209 | Snap MV Threshold | PER | Config | float32 | R/W | 2208 | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | 42210 | [8 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 | 42211 | Snap Rog Threshold | PER | Config | float32 | R/W | 2210 | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | 42212 | [8 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 | 42213 | Snap Volt Threshold | V | Config | float32 | R/W | 2212 | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | 42214 | [8 empty] | system |  |  | ALL
Communications Mode | 2214 | 42215 | Communications Mode |  | Config |  |  | 2214 | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 | 42216 | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W | 2215 | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | 42217 | [8 empty] | system |  |  | ALL
Voltage Input Element | 2217 | 42218 | Element Voltage Input |  | Config | enum16 | R/W | 62217 | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 | 42219 | CT1 RANGE | A | Config | float32 | R/W | 62218 | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | 42220 | [8 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 | 42221 | Voltage Reference for CT1 |  | Config | enum16 | R/W | 62220 | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 | 42222 | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W | 62221 | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | 42223 | [8 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 | 42224 | CT1 TYPE |  | Config | enum16 | R/W | 62223 | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 | 42225 | CT1 PHASE SHIFT | Deg | Config | float32 | R/W | 62224 | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | 42226 | [8 empty] | element |  |  | ALL
CH1 CT Sign | 2226 | 42227 | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W | 62226 | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 | 42228 | CT2 RANGE | A | Config | float32 | R/W | 62227 | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | 42229 | [8 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 | 42230 | Voltage Reference for CT2 |  | Config | enum16 | R/W | 62229 | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 | 42231 | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W | 62230 | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | 42232 | [8 empty] | element | >0 |  | ALL
CH2 CT type | 2232 | 42233 | CT2 TYPE |  | Config | enum16 | R/W | 62232 | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 | 42234 | CT2 PHASE SHIFT | Deg | Config | float32 | R/W | 62233 | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | 42235 | [8 empty] | element |  |  | ALL
CH2 CT Sign | 2235 | 42236 | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W | 62235 | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 | 42237 | CT3 INTEGER | A | Config | float32 | R/W | 62236 | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | 42238 | [8 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 | 42239 | Voltage Reference for CT3 |  | Config | enum16 | R/W | 62238 | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 | 42240 | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W | 62239 | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | 42241 | [8 empty] | element | >0 |  | ALL
CH3 CT type | 2241 | 42242 | CT3 TYPE |  | Config | enum16 | R/W | 62241 | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 | 42243 | CT3 PHASE SHIFT | Deg | Config | float32 | R/W | 62242 | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | 42244 | [8 empty] | element |  |  | ALL
CH3 CT Sign | 2244 | 42245 | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W | 62244 | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 | 42246 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 | 42247 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 | 42248 | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 | 42249 | PF Sign Convention |  | Config | uint16 | R/W | 2248 | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 | 42250 | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 | 42251 | BACnet UDP Port |  | Config | uint16 | R/W | 2250 | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 | 42252 | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 | 42253 | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | 42254 | [8 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 | 42261 | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | 42262 | [11 empty] | ALL
BACnet Max Info Frames | 2262 | 42263 | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 | 42264 | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 | 42265 | BBMD IP Address |  | Config | string(16) | R/W | 2264 | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | 42266 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | 42267 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | 42268 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | 42269 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | 42270 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | 42271 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | 42272 | [9 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 | 42273 | LCD/WebApp Read Password |  | Config | uint16 | R/W | 2272 | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 | 42274 | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 | 42275 | Customer Line frequency |  | Config | float | R/W | 2274 | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | 42276 | [10 empty] | Reserved | ALL
Communications Interface Configured | 2276 | 42277 | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 | 42278 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 | 42279 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 | 42280 | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 | 42281 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 | 42282 | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 | 42283 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 | 42284 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 | 42285 | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 | 42286 | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 | 42287 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 | 42288 | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 | 42289 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 | 42290 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 | 42291 | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 | 42292 | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | 42293 | [11 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 | 42294 | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | 42295 | [11 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 | 42296 | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 | 42297 | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - | METROLOGY POINTS | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 | 42301 | Displacement PF Avg Element | dPF | Metrology | float32 | R | 62300 | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | 42302 | [11 empty] | ALL
Displacement PF CH1 (MSW) | 2302 | 42303 | Displacement PF CH1 (A) | dPF | Metrology | float32 | R | 62302 | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | 42304 | [11 empty] | ALL
Displacement PF CH2 (MSW) | 2304 | 42305 | Displacement PF CH2 (B) | dPF | Metrology | float32 | R | 62304 | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | 42306 | [11 empty] | ALL
Displacement PF CH3 (MSW) | 2306 | 42307 | Displacement PF CH3 (C) | dPF | Metrology | float32 | R | 62306 | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | 42308 | [11 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 | 42309 | Avg Apparent PF Element | aPF | Metrology | float32 | R | 62308 | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | 42310 | [11 empty] | ALL
Apparent PF CH1 (MSW) | 2310 | 42311 | Apparent PF CH1 (A) | aPF | Metrology | float32 | R | 62310 | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | 42312 | [11 empty] | ALL
Apparent PF CH2 (MSW) | 2312 | 42313 | Apparent PF CH2 (B) | aPF | Metrology | float32 | R | 62312 | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | 42314 | [11 empty] | ALL
Apparent PF CH3 (MSW) | 2314 | 42315 | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R | 62314 | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | 42316 | [11 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 | 42317 | Distortion PF Avg Element | tPF | Metrology | float32 | R | 62316 | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | 42318 | [11 empty] | ALL
Distortion PF CH1 (MSW) | 2318 | 42319 | Distortion PF CH1 (A) | tPF | Metrology | float32 | R | 62318 | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | 42320 | [11 empty] | ALL
Distortion PF CH2 (MSW) | 2320 | 42321 | Distortion PF CH2 (B) | tPF | Metrology | float32 | R | 62320 | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | 42322 | [11 empty] | ALL
Distortion PF CH3 (MSW) | 2322 | 42323 | Distortion PF CH3 (C) | tPF | Metrology | float32 | R | 62322 | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | 42324 | [11 empty] | ALL
THD Avg Element (MSW) | 2324 | 42325 | THD Avg Element | % | Metrology | float32 | R | 62324 | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | 42326 | [11 empty] | ALL
THD CH1 (MSW) | 2326 | 42327 | THD CH1 (A) | % | Metrology | float32 | R | 62326 | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | 42328 | [11 empty] | ALL
THD CH2 (MSW) | 2328 | 42329 | THD CH2 (B) | % | Metrology | float32 | R | 62328 | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | 42330 | [11 empty] | ALL
THD CH3 (MSW) | 2330 | 42331 | THD CH3 (C) | % | Metrology | float32 | R | 62330 | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | 42332 | [11 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 | 42333 | Power Demand Max Interval Element | kW | Metrology | float32 | R | 62332 | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | 42334 | [11 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 | 42335 | Power Demand This Interval Element | kW | Metrology | float32 | R | 62334 | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | 42336 | [11 empty] | ALL
VA Peak Demand Element (MSW) | 2336 | 42337 | VA Demand Max Interval Element | kVA | Metrology | float32 | R | 62336 | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | 42338 | [11 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 | 42339 | VA Demand This Interval Element | kVA | Metrology | float32 | R | 62338 | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | 42340 | [11 empty] | ALL
Not Used | 2340 | 42341 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 | 42342 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 | 42343 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 | 42344 | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 | 42345 | Energy Net Sum Element | kWh | Metrology | float32 | R | 62344 | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | 42346 | [8 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 | 42347 | Energy Net CH1 | kWh | Metrology | float32 | R | 62346 | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | 42348 | [8 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 | 42349 | Energy Net CH2 | kWh | Metrology | float32 | R | 62348 | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | 42350 | [8 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 | 42351 | Energy Net CH3 | kWh | Metrology | float32 | R | 62350 | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | 42352 | [8 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 | 42353 | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R | 62352 | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | 42354 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 | 42355 | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R | 62354 | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | 42356 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 | 42357 | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R | 62356 | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | 42358 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 | 42359 | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R | 62358 | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | 42360 | [8 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 | 42361 | VARh Net Sum Element | kVArh | Metrology | float32 | R | 62360 | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | 42362 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 | 42363 | VARh Net CH1 | kVArh | Metrology | float32 | R | 62362 | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | 42364 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 | 42365 | VARh Net CH2 | kVArh | Metrology | float32 | R | 62364 | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | 42366 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 | 42367 | VARh Net CH3 | kVArh | Metrology | float32 | R | 62366 | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | 42368 | [8 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 | 42369 | Time Since Reset MSW | Sec | Metrology | uint32 |  | 2368 | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 | 42370 | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 | 42371 | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 | 42372 | CH1 Angle | Deg | Metrology | float32 | R | 62371 | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | 42373 | [8 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 | 42374 | CH2 Angle | Deg | Metrology | float32 | R | 62373 | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | 42375 | [8 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 | 42376 | CH3 Angle | Deg | Metrology | float32 | R | 62375 | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | 42377 | [11 empty] | ALL
Phase Chek System Status | 2377 | 42378 | System Phase Check Status |  | Metrology | bitfield16 | R | 2377 | BV | Phase Check System Status | system | 0,1 | 0 (All Channels OK), 1(Somewhere a channel is reading a dPF < 0.55), check register 2378 for each Element | ALL
Phase Chek Element Status | 2378 | 42379 | Element Phase Check Status |  | Metrology | bitfield16 | R | 62378 | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 | 42380 | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 | 42381 | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 | 42382 | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 | 42392 | Element Angle |  | Metrology | float | R | 62391 | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | 42393 | [11 empty] | ALL
PULSE INPUTS | - | - | PULSE INPUTS | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 | 42401 | Pulse Input 1 Enable |  | Config | uint16 | R/W | 2400 | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 | 42402 | Pulse Input 1 Scale Factor |  | Config | float32 | R/W | 2401 | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 | 42403 |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 | 42404 | Pulse Input 1 Units |  | Config | string(4) | R/W | 2403 | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 | 42405 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 | 42406 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 | 42407 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 | 42408 | Pulse Input 1 Accumulator |  | Metrology | float32 | R | 2407 | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | 42409 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 | 42410 | Pulse Input 1 Accumulator Clear |  | User | unit16 | W | 2409 | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 | 42411 | Pulse Input 2 Enable |  | Config | uint16 | R/W | 2410 | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 | 42412 | Pulse Input 2 Scale Factor |  | Config | float32 | R/W | 2411 | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | 42413 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 | 42414 | Pulse Input 2 Units |  | Config | string(4) | R/W | 2413 | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 | 42415 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 | 42416 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 | 42417 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 | 42418 | Pulse Input 2 Accumulator |  | Metrology | float32 | R | 2417 | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | 42419 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 | 42420 | Pulse Input 2 Accumulator Clear |  | User | unit16 | W | 2419 | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 | 42421 | Pulse Input 3 Enable |  | Config | uint16 | R/W | 2420 | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 | 42422 | Pulse Input 3 Scale Factor |  | Config | float32 | R/W | 2421 | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | 42423 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 | 42424 | Pulse Input 3 Units |  | Config | string(4) | R/W | 2423 | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 | 42425 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 | 42426 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 | 42427 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 | 42428 | Pulse Input 3 Accumulator |  | Metrology | float32 | R | 2427 | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | 42429 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 | 42430 | Pulse Input 3 Accumulator Clear |  | User |  | W | 2429 | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 | 42431 | Pulse Input 4 Enable |  | Config | uint16 | R/W | 2430 | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 | 42432 | Pulse Input 4 Scale Factor |  | Config | float32 | R/W | 2431 | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | 42433 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 | 42434 | Pulse Input 4 Units |  | Config | string(4) | R/W | 2433 | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 | 42435 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 | 42436 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 | 42437 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 | 42438 | Pulse Input 4 Accumulator |  | Metrology | float32 | R | 2437 | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | 42439 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 | 42440 | Pulse Input 4 Accumulator Clear |  | User | unit16 | W | 2439 | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - | ALARMS | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 | 42452 | State of Alarm |  | Metrology | uint16 | R/W | 2451 | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 | 42453 | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 | 42454 | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 | 42455 | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 | 42456 | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 | 42457 | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 | 42458 | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 | 42459 | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W | 2458 | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 | 42460 | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W | 2459 | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Range Vin1 L1N Under | 2460 | 42461 | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W | 2460 | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 | 42462 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2N Under | 2462 | 42463 | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W | 2462 | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 | 42464 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3N Under | 2464 | 42465 | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W | 2464 | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 | 42466 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L1L2 Under | 2466 | 42467 | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W | 2466 | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 | 42468 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2L3 Under | 2468 | 42469 | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W | 2468 | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 | 42470 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3L1 Under | 2470 | 42471 | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W | 2470 | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 | 42472 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin2 L1N Under | 2472 | 42473 | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W | 2472 | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 | 42474 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2N Under | 2474 | 42475 | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W | 2474 | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 | 42476 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3N Under | 2476 | 42477 | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W | 2476 | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 | 42478 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L1L2 Under | 2478 | 42479 | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W | 2478 | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 | 42480 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2L3 Under | 2480 | 42481 | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W | 2480 | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 | 42482 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3L1 Under | 2482 | 42483 | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W | 2482 | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 | 42484 | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 | 42485 | Voltage Alarm Persistence | Sec | Config | uint16 | R/W | 2484 | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 | 42486 | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R | 2485 | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 | 42487 | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 | 42488 | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R | 2487 | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 | 42489 | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 | 42490 | Real Time Clock MSW |  | Config | uint16 | R/W | 2489 | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 | 42491 | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - | USER CONFIG POINTS 2 | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 | 42602 | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 | 42603 | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 | 42604 | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 | 42605 | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 | 42606 | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 | 42607 | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 | 42608 | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 | 42609 | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 | 42610 | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 | 42611 | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 | 42612 | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 | 42613 | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 | 42614 | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 | 42615 | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 | 42616 | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 | 42617 | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 | 42618 | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 | 42619 | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 | 42620 | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 | 42621 | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 | 42622 | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 | 42623 | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 | 42624 | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 | 42625 | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 | 42626 | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 | 42627 | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 | 42628 | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 | 42629 | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 | 42630 | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 | 42631 | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 | 42632 | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 | 42633 | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 | 42634 | BACnet Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | 2634 | 42635 | BACnet Description 1 | [8 empty] | 2 Char |  | ALL
BACnet Description 2 | 2635 | 42636 | BACnet Description 2 | [8 empty] | 2 Char |  | ALL
BACnet Description 3 | 2636 | 42637 | BACnet Description 3 | [8 empty] | 2 Char |  | ALL
BACnet Description 4 | 2637 | 42638 | BACnet Description 4 | [8 empty] | 2 Char |  | ALL
BACnet Description 5 | 2638 | 42639 | BACnet Description 5 | [8 empty] | 2 Char |  | ALL
BACnet Description 6 | 2639 | 42640 | BACnet Description 6 | [8 empty] | 2 Char |  | ALL
BACnet Description 7 | 2640 | 42641 | BACnet Description 7 | [8 empty] | 2 Char |  | ALL
BACnet Description 8 | 2641 | 42642 | BACnet Description 8 | [8 empty] | 2 Char |  | ALL
BACnet Description 9 | 2642 | 42643 | BACnet Description 9 | [8 empty] | 2 Char |  | ALL
BACnet Description 10 | 2643 | 42644 | BACnet Description 10 | [8 empty] | 2 Char |  | ALL
BACnet Description 11 | 2644 | 42645 | BACnet Description 11 | [8 empty] | 2 Char |  | ALL
BACnet Description 12 | 2645 | 42646 | BACnet Description 12 | [8 empty] | 2 Char |  | ALL
BACnet Description 13 | 2646 | 42647 | BACnet Description 13 | [8 empty] | 2 Char |  | ALL
BACnet Description 14 | 2647 | 42648 | BACnet Description 14 | [8 empty] | 2 Char |  | ALL
BACnet Description 15 | 2648 | 42649 | BACnet Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
VERIS EMULATION LEGACY REGISTERS | - | - | VERIS EMULATION LEGACY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Veris Emulation Mode | 2200 | 42201 | Set to Veris Emulation Mode |  | Config | uint16 | R/W |  |  |  | system | 0-1 | 1 = Report Slave ID as Veris Model H8036 | ALL
kWh System LSW | 0 | 40001 | kWh System LSW | kWh | Veris | uint32 | R |  |  |  | element |  |  | ALL
kWh System MSW | 1 | 40002 | kWh System MSW | kWh | Veris |  | R |  |  |  | element |  |  | ALL
kW System | 2 | 40003 | kW System | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVAR System | 3 | 40004 | kVAR System | kVAR | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVA System | 4 | 40005 | kVA System | kVA | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF System | 5 | 40006 | Apparent PF System | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts Line to Line Avg | 6 | 40007 | Volts Line to Line Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts Line to Neutral Avg | 7 | 40008 | Volts Line to Neutral Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps System Avg | 8 | 40009 | Amps System Avg | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L1 | 9 | 40010 | kW L1 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L2 | 10 | 40011 | kW L2 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L3 | 11 | 40012 | kW L3 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L1 | 12 | 40013 | Apparent PF L1 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L2 | 13 | 40014 | Apparent PF L2 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L3 | 14 | 40015 | Apparent PF L3 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts L1 to L2 | 15 | 40016 | Volts L1 to L2 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to L3 | 16 | 40017 | Volts L2 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to L3 | 17 | 40018 | Volts L1 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to Neutral | 18 | 40019 | Volts L1 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to Neutral | 19 | 40020 | Volts L2 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L3 to Neutral | 20 | 40021 | Volts L3 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps L1 | 21 | 40022 | Amps L1 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L2 | 22 | 40023 | Amps L2 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L3 | 23 | 40024 | Amps L3 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW System Avg | 24 | 40025 | kW System Avg | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Now | 25 | 40026 | kW Demand Sys Now (was Min) | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Max | 26 | 40027 | kW Demand Sys Max | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL

## H
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS --> | 8
BACNET OBJECT FLOOR --> | 70000
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 | 41002 | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | 41003 | [8 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 | 41004 | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 | 41005 | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 | 41006 | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | 41007 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | 41008 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | 41009 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | 41010 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | 41011 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | 41012 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | 41013 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | 41014 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | 41015 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | 41016 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | 41017 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | 41018 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | 41019 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | 41020 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | 41021 | [8 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 | 41022 | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | 41023 | [8 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | 41024 | [8 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | 41025 | [8 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | 41026 | [8 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | 41027 | [8 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | 41028 | [8 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | 41029 | [8 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | 41030 | [8 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | 41031 | [8 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | 41032 | [8 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | 41033 | [8 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | 41034 | [8 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | 41035 | [8 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | 41036 | [8 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | 41037 | [8 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 | 41038 | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | 41039 | [8 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | 41040 | [8 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | 41041 | [8 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | 41042 | [8 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | 41043 | [8 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | 41044 | [8 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | 41045 | [8 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 | 41046 | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | 41047 | [8 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | 41048 | [8 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | 41049 | [8 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | 41050 | [8 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | 41051 | [8 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | 41052 | [8 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | 41053 | [8 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 | 41054 | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | 41055 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | 41056 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | 41057 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | 41058 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | 41059 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | 41060 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | 41061 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | 41062 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | 41063 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | 41064 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | 41065 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | 41066 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | 41067 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | 41068 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | 41069 | [8 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 | 41070 | Modbus Device Address |  |  | unit16 | R/W | 1069 | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | 41071 | [8 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 | 41072 | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 | 41073 | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 | 41074 | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | 41075 | [8 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | 41076 | [8 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | 41077 | [8 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 | 41078 | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 | 41079 | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 | 41080 | IP Address |  |  | string(8) | R/W | 1079 | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | 41081 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | 41082 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | 41083 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | 41084 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | 41085 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | 41086 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | 41087 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 | 41088 | Netmask |  |  | string(8) | R/W | 1087 | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | 41089 | [8 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | 41090 | [8 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | 41091 | [8 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | 41092 | [8 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | 41093 | [8 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | 41094 | [8 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | 41095 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 | 41096 | Gateway |  |  | string(8) | R/W | 1095 | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | 41097 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | 41098 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | 41099 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | 41100 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | 41101 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | 41102 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | 41103 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 | 41104 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | 41105 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | 41106 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | 41107 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | 41108 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | 41109 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | 41110 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | 41111 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 | 41112 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | 41113 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | 41114 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | 41115 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | 41116 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | 41117 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | 41118 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | 41119 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 | 41120 | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | 41121 | [8 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | 41122 | [8 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | 41123 | [8 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 | 41124 | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | 41125 | [9 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 | 41126 | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 | 41127 | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 | 41128 | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | 41129 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | 41130 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | 41131 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 | 41132 | Interface baud rate in bits per second |  |  | uint32 | R/W | 1131 | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | 41133 | [8 empty] | system |  |  | ALL
SERIAL BITS | 1133 | 41134 | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 | 41135 | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 | 41136 | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 | 41137 | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 | 41138 | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 | 41139 | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 | 41140 | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 | 41141 | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 | 41142 | Current Avg Element | A | Metrology | float32 | R | 71141 | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | 41143 | [8 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 | 41144 | Current CH1 (A) | A | Metrology | float32 | R | 71143 | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | 41145 | [8 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 | 41146 | Current CH2 (B) | A | Metrology | float32 | R | 71145 | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | 41147 | [8 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 | 41148 | Current CH3 (C) | A | Metrology | float32 | R | 71147 | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | 41149 | [8 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 | 41150 | Voltage L to N Avg Element | V | Metrology | float32 | R | 71149 | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | 41151 | [8 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 | 41152 | Voltage L1 to N (AN) | V | Metrology | float32 | R | 71151 | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | 41153 | [8 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 | 41154 | Voltage L2 to N (BN) | V | Metrology | float32 | R | 71153 | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | 41155 | [8 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 | 41156 | Voltage L3 to N (CN) | V | Metrology | float32 | R | 71155 | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | 41157 | [8 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 | 41158 | Voltage L to L Avg Element | V | Metrology | float32 | R | 71157 | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | 41159 | [8 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 | 41160 | Voltage L1 to L2 (AB) | V | Metrology | float32 | R | 71159 | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | 41161 | [8 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 | 41162 | Voltage L2 to L3 (BC) | V | Metrology | float32 | R | 71161 | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | 41163 | [8 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 | 41164 | Voltage L3 to L1 (CA) | V | Metrology | float32 | R | 71163 | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | 41165 | [8 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 | 41166 | Line Frequency | Hz | Metrology | float32 | R | 71165 | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | 41167 | [8 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 | 41168 | Power Sum Element | kW | Metrology | float32 | R | 71167 | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | 41169 | [8 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 | 41170 | Power CH1 (A) | kW | Metrology | float32 | R | 71169 | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | 41171 | [8 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 | 41172 | Power CH2 (B) | kW | Metrology | float32 | R | 71171 | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | 41173 | [8 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 | 41174 | Power CH3 (C) | kW | Metrology | float32 | R | 71173 | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | 41175 | [8 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 | 41176 | VA Sum Element | kVA | Metrology | float32 | R | 71175 | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | 41177 | [8 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 | 41178 | VA CH1 (A) | kVA | Metrology | float32 | R | 71177 | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | 41179 | [8 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 | 41180 | VA CH2 (B) | kVA | Metrology | float32 | R | 71179 | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | 41181 | [8 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 | 41182 | VA CH3 (C) | kVA | Metrology | float32 | R | 71181 | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | 41183 | [8 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 | 41184 | VAR Sum Element | kVAr | Metrology | float32 | R | 71183 | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | 41185 | [8 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 | 41186 | VAR CH1 (A) | kVAr | Metrology | float32 | R | 71185 | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | 41187 | [8 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 | 41188 | VAR CH2 (B) | kVAr | Metrology | float32 | R | 71187 | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | 41189 | [8 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 | 41190 | VAR CH3 (C) | kVAr | Metrology | float32 | R | 71189 | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | 41191 | [8 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 | 41192 | Apparent PF Avg Element | PF | Metrology | float32 | R | 71191 | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | 41193 | [8 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 | 41194 | Apparent PF CH1 (A) | PF | Metrology | float32 | R | 71193 | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | 41195 | [8 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 | 41196 | Apparent PF CH2 (B) | PF | Metrology | float32 | R | 71195 | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | 41197 | [8 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 | 41198 | Apparent PF CH3 ( C) | PF | Metrology | float32 | R | 71197 | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | 41199 | [8 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 | 41200 | Exported Energy Sum Element | kWh | Metrology | float32 | R | 71199 | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | 41201 | [8 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 | 41202 | Exported Energy CH1 (A) | kWh | Metrology | float32 | R | 71201 | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | 41203 | [8 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 | 41204 | Exported Energy CH2 (B) | kWh | Metrology | float32 | R | 71203 | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | 41205 | [8 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 | 41206 | Exported Energy CH3 (C) | kWh | Metrology | float32 | R | 71205 | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | 41207 | [8 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 | 41208 | Imported Energy Sum Element | kWh | Metrology | float32 | R | 71207 | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | 41209 | [8 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 | 41210 | Imported Energy CH1 (A) | kWh | Metrology | float32 | R | 71209 | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | 41211 | [8 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 | 41212 | Imported Energy CH2 (B) | kWh | Metrology | float32 | R | 71211 | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | 41213 | [8 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 | 41214 | Imported Energy CH3 (C) | kWh | Metrology | float32 | R | 71213 | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | 41215 | [8 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 | 41216 | Exported VAh Sum Element | kVAh | Metrology | float32 | R | 71215 | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | 41217 | [8 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 | 41218 | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R | 71217 | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | 41219 | [8 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 | 41220 | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R | 71219 | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | 41221 | [8 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 | 41222 | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R | 71221 | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | 41223 | [8 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 | 41224 | Imported VAh Sum Element | kVAh | Metrology | float32 | R | 71223 | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | 41225 | [8 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 | 41226 | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R | 71225 | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | 41227 | [8 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 | 41228 | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R | 71227 | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | 41229 | [8 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 | 41230 | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R | 71229 | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | 41231 | [8 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 | 41232 | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R | 71231 | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | 41233 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 | 41234 | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R | 71233 | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | 41235 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 | 41236 | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R | 71235 | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | 41237 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 | 41238 | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R | 71237 | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | 41239 | [8 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 | 41240 | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R | 71239 | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | 41241 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 | 41242 | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R | 71241 | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | 41243 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 | 41244 | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R | 71243 | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | 41245 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 | 41246 | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R | 71245 | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | 41247 | [8 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 | 41248 | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R | 71247 | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | 41249 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 | 41250 | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R | 71249 | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | 41251 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 | 41252 | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R | 71251 | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | 41253 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 | 41254 | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R | 71253 | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | 41255 | [8 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 | 41256 | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R | 71255 | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | 41257 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 | 41258 | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R | 71257 | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | 41259 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 | 41260 | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R | 71259 | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | 41261 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 | 41262 | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R | 71261 | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | 41263 | [8 empty] | element |  |  | ALL
Events MSW | 1263 | 41264 | Events MSW |  |  | bitfield32 | R | 1263 | AI | Events | system |  |  | ALL
Events LSW | 1264 | 41265 | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 | 41266 | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 | 41267 | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
FACTORY REGISTERS | - | - | FACTORY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Factory Unlock Register | 2000 | 42001 | Factory Unlock Register |  | Factory | unit16 | R/W |  |  |  | system |  | Reserved | ALL
Factory Reset | 2001 | 42002 | Factory Reset |  | Factory | unit16 | R/W |  |  |  | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
OEM Vendor ID | 2002 | 42003 | OEM Vendor ID |  | Factory | unit16 | R |  |  |  | system |  | Reserved | ALL
FACTORY_CONFIG | 2003 | 42004 | Factory Config |  | Factory | unit16 | R |  |  |  | system | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable | ALL
USER COMMAND POINTS | - | - | USER COMMAND POINTS | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 | 42101 | Reset (software) processor |  | User | unit16 | W | 2100 | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 | 42102 | Clear all accumulated measurements (CAM) |  | User | unit16 | W | 2101 | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 | 42103 | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W | 72102 | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 | 42104 | Clear Peak Demand Element |  | User | unit16 | W | 72103 | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 | 42105 | Clear Peak Demand All |  | User | unit16 | W | 2104 | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 | 42106 | Reset to User Defaults |  | User | unit16 | W | 2105 | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - | USER CONFIG POINTS | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 | 42202 | Sliding or Fixed |  | Config | enum16 | R | 2201 | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 | 42203 | Demand Window | Min | Config | uint16 | R | 2202 | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 | 42204 | Volt Multiplier VINPUT1 |  | Config | float32 | R/W | 2203 | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | 42205 | [8 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 | 42206 | Volt Multiplier VINPUT2 |  | Config | float32 | R/W | 2205 | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | 42207 | [8 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 | 42208 | Service Type |  | Config | enum16 | R/W | 72207 | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 | 42209 | Snap MV Threshold | PER | Config | float32 | R/W | 2208 | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | 42210 | [8 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 | 42211 | Snap Rog Threshold | PER | Config | float32 | R/W | 2210 | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | 42212 | [8 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 | 42213 | Snap Volt Threshold | V | Config | float32 | R/W | 2212 | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | 42214 | [8 empty] | system |  |  | ALL
Communications Mode | 2214 | 42215 | Communications Mode |  | Config |  |  | 2214 | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 | 42216 | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W | 2215 | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | 42217 | [8 empty] | system |  |  | ALL
Voltage Input Element | 2217 | 42218 | Element Voltage Input |  | Config | enum16 | R/W | 72217 | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 | 42219 | CT1 RANGE | A | Config | float32 | R/W | 72218 | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | 42220 | [8 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 | 42221 | Voltage Reference for CT1 |  | Config | enum16 | R/W | 72220 | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 | 42222 | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W | 72221 | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | 42223 | [8 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 | 42224 | CT1 TYPE |  | Config | enum16 | R/W | 72223 | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 | 42225 | CT1 PHASE SHIFT | Deg | Config | float32 | R/W | 72224 | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | 42226 | [8 empty] | element |  |  | ALL
CH1 CT Sign | 2226 | 42227 | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W | 72226 | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 | 42228 | CT2 RANGE | A | Config | float32 | R/W | 72227 | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | 42229 | [8 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 | 42230 | Voltage Reference for CT2 |  | Config | enum16 | R/W | 72229 | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 | 42231 | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W | 72230 | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | 42232 | [8 empty] | element | >0 |  | ALL
CH2 CT type | 2232 | 42233 | CT2 TYPE |  | Config | enum16 | R/W | 72232 | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 | 42234 | CT2 PHASE SHIFT | Deg | Config | float32 | R/W | 72233 | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | 42235 | [8 empty] | element |  |  | ALL
CH2 CT Sign | 2235 | 42236 | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W | 72235 | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 | 42237 | CT3 INTEGER | A | Config | float32 | R/W | 72236 | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | 42238 | [8 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 | 42239 | Voltage Reference for CT3 |  | Config | enum16 | R/W | 72238 | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 | 42240 | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W | 72239 | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | 42241 | [8 empty] | element | >0 |  | ALL
CH3 CT type | 2241 | 42242 | CT3 TYPE |  | Config | enum16 | R/W | 72241 | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 | 42243 | CT3 PHASE SHIFT | Deg | Config | float32 | R/W | 72242 | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | 42244 | [8 empty] | element |  |  | ALL
CH3 CT Sign | 2244 | 42245 | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W | 72244 | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 | 42246 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 | 42247 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 | 42248 | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 | 42249 | PF Sign Convention |  | Config | uint16 | R/W | 2248 | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 | 42250 | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 | 42251 | BACnet UDP Port |  | Config | uint16 | R/W | 2250 | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 | 42252 | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 | 42253 | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | 42254 | [8 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 | 42261 | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | 42262 | [11 empty] | ALL
BACnet Max Info Frames | 2262 | 42263 | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 | 42264 | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 | 42265 | BBMD IP Address |  | Config | string(16) | R/W | 2264 | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | 42266 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | 42267 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | 42268 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | 42269 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | 42270 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | 42271 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | 42272 | [9 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 | 42273 | LCD/WebApp Read Password |  | Config | uint16 | R/W | 2272 | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 | 42274 | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 | 42275 | Customer Line frequency |  | Config | float | R/W | 2274 | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | 42276 | [10 empty] | Reserved | ALL
Communications Interface Configured | 2276 | 42277 | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 | 42278 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 | 42279 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 | 42280 | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 | 42281 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 | 42282 | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 | 42283 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 | 42284 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 | 42285 | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 | 42286 | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 | 42287 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 | 42288 | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 | 42289 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 | 42290 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 | 42291 | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 | 42292 | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | 42293 | [11 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 | 42294 | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | 42295 | [11 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 | 42296 | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 | 42297 | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - | METROLOGY POINTS | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 | 42301 | Displacement PF Avg Element | dPF | Metrology | float32 | R | 72300 | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | 42302 | [11 empty] | ALL
Displacement PF CH1 (MSW) | 2302 | 42303 | Displacement PF CH1 (A) | dPF | Metrology | float32 | R | 72302 | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | 42304 | [11 empty] | ALL
Displacement PF CH2 (MSW) | 2304 | 42305 | Displacement PF CH2 (B) | dPF | Metrology | float32 | R | 72304 | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | 42306 | [11 empty] | ALL
Displacement PF CH3 (MSW) | 2306 | 42307 | Displacement PF CH3 (C) | dPF | Metrology | float32 | R | 72306 | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | 42308 | [11 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 | 42309 | Avg Apparent PF Element | aPF | Metrology | float32 | R | 72308 | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | 42310 | [11 empty] | ALL
Apparent PF CH1 (MSW) | 2310 | 42311 | Apparent PF CH1 (A) | aPF | Metrology | float32 | R | 72310 | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | 42312 | [11 empty] | ALL
Apparent PF CH2 (MSW) | 2312 | 42313 | Apparent PF CH2 (B) | aPF | Metrology | float32 | R | 72312 | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | 42314 | [11 empty] | ALL
Apparent PF CH3 (MSW) | 2314 | 42315 | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R | 72314 | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | 42316 | [11 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 | 42317 | Distortion PF Avg Element | tPF | Metrology | float32 | R | 72316 | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | 42318 | [11 empty] | ALL
Distortion PF CH1 (MSW) | 2318 | 42319 | Distortion PF CH1 (A) | tPF | Metrology | float32 | R | 72318 | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | 42320 | [11 empty] | ALL
Distortion PF CH2 (MSW) | 2320 | 42321 | Distortion PF CH2 (B) | tPF | Metrology | float32 | R | 72320 | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | 42322 | [11 empty] | ALL
Distortion PF CH3 (MSW) | 2322 | 42323 | Distortion PF CH3 (C) | tPF | Metrology | float32 | R | 72322 | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | 42324 | [11 empty] | ALL
THD Avg Element (MSW) | 2324 | 42325 | THD Avg Element | % | Metrology | float32 | R | 72324 | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | 42326 | [11 empty] | ALL
THD CH1 (MSW) | 2326 | 42327 | THD CH1 (A) | % | Metrology | float32 | R | 72326 | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | 42328 | [11 empty] | ALL
THD CH2 (MSW) | 2328 | 42329 | THD CH2 (B) | % | Metrology | float32 | R | 72328 | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | 42330 | [11 empty] | ALL
THD CH3 (MSW) | 2330 | 42331 | THD CH3 (C) | % | Metrology | float32 | R | 72330 | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | 42332 | [11 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 | 42333 | Power Demand Max Interval Element | kW | Metrology | float32 | R | 72332 | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | 42334 | [11 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 | 42335 | Power Demand This Interval Element | kW | Metrology | float32 | R | 72334 | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | 42336 | [11 empty] | ALL
VA Peak Demand Element (MSW) | 2336 | 42337 | VA Demand Max Interval Element | kVA | Metrology | float32 | R | 72336 | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | 42338 | [11 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 | 42339 | VA Demand This Interval Element | kVA | Metrology | float32 | R | 72338 | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | 42340 | [11 empty] | ALL
Not Used | 2340 | 42341 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 | 42342 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 | 42343 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 | 42344 | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 | 42345 | Energy Net Sum Element | kWh | Metrology | float32 | R | 72344 | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | 42346 | [8 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 | 42347 | Energy Net CH1 | kWh | Metrology | float32 | R | 72346 | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | 42348 | [8 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 | 42349 | Energy Net CH2 | kWh | Metrology | float32 | R | 72348 | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | 42350 | [8 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 | 42351 | Energy Net CH3 | kWh | Metrology | float32 | R | 72350 | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | 42352 | [8 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 | 42353 | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R | 72352 | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | 42354 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 | 42355 | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R | 72354 | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | 42356 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 | 42357 | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R | 72356 | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | 42358 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 | 42359 | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R | 72358 | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | 42360 | [8 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 | 42361 | VARh Net Sum Element | kVArh | Metrology | float32 | R | 72360 | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | 42362 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 | 42363 | VARh Net CH1 | kVArh | Metrology | float32 | R | 72362 | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | 42364 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 | 42365 | VARh Net CH2 | kVArh | Metrology | float32 | R | 72364 | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | 42366 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 | 42367 | VARh Net CH3 | kVArh | Metrology | float32 | R | 72366 | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | 42368 | [8 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 | 42369 | Time Since Reset MSW | Sec | Metrology | uint32 |  | 2368 | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 | 42370 | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 | 42371 | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 | 42372 | CH1 Angle | Deg | Metrology | float32 | R | 72371 | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | 42373 | [8 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 | 42374 | CH2 Angle | Deg | Metrology | float32 | R | 72373 | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | 42375 | [8 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 | 42376 | CH3 Angle | Deg | Metrology | float32 | R | 72375 | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | 42377 | [11 empty] | ALL
Phase Chek System Status | 2377 | 42378 | System Phase Check Status |  | Metrology | bitfield16 | R | 2377 | BV | Phase Check System Status | system | 0,1 | 0 (All Channels OK), 1(Somewhere a channel is reading a dPF < 0.55), check register 2378 for each Element | ALL
Phase Chek Element Status | 2378 | 42379 | Element Phase Check Status |  | Metrology | bitfield16 | R | 72378 | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 | 42380 | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 | 42381 | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 | 42382 | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 | 42392 | Element Angle |  | Metrology | float | R | 72391 | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | 42393 | [11 empty] | ALL
PULSE INPUTS | - | - | PULSE INPUTS | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 | 42401 | Pulse Input 1 Enable |  | Config | uint16 | R/W | 2400 | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 | 42402 | Pulse Input 1 Scale Factor |  | Config | float32 | R/W | 2401 | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 | 42403 |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 | 42404 | Pulse Input 1 Units |  | Config | string(4) | R/W | 2403 | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 | 42405 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 | 42406 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 | 42407 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 | 42408 | Pulse Input 1 Accumulator |  | Metrology | float32 | R | 2407 | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | 42409 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 | 42410 | Pulse Input 1 Accumulator Clear |  | User | unit16 | W | 2409 | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 | 42411 | Pulse Input 2 Enable |  | Config | uint16 | R/W | 2410 | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 | 42412 | Pulse Input 2 Scale Factor |  | Config | float32 | R/W | 2411 | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | 42413 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 | 42414 | Pulse Input 2 Units |  | Config | string(4) | R/W | 2413 | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 | 42415 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 | 42416 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 | 42417 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 | 42418 | Pulse Input 2 Accumulator |  | Metrology | float32 | R | 2417 | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | 42419 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 | 42420 | Pulse Input 2 Accumulator Clear |  | User | unit16 | W | 2419 | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 | 42421 | Pulse Input 3 Enable |  | Config | uint16 | R/W | 2420 | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 | 42422 | Pulse Input 3 Scale Factor |  | Config | float32 | R/W | 2421 | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | 42423 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 | 42424 | Pulse Input 3 Units |  | Config | string(4) | R/W | 2423 | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 | 42425 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 | 42426 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 | 42427 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 | 42428 | Pulse Input 3 Accumulator |  | Metrology | float32 | R | 2427 | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | 42429 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 | 42430 | Pulse Input 3 Accumulator Clear |  | User |  | W | 2429 | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 | 42431 | Pulse Input 4 Enable |  | Config | uint16 | R/W | 2430 | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 | 42432 | Pulse Input 4 Scale Factor |  | Config | float32 | R/W | 2431 | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | 42433 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 | 42434 | Pulse Input 4 Units |  | Config | string(4) | R/W | 2433 | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 | 42435 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 | 42436 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 | 42437 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 | 42438 | Pulse Input 4 Accumulator |  | Metrology | float32 | R | 2437 | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | 42439 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 | 42440 | Pulse Input 4 Accumulator Clear |  | User | unit16 | W | 2439 | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - | ALARMS | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 | 42452 | State of Alarm |  | Metrology | uint16 | R/W | 2451 | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 | 42453 | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 | 42454 | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 | 42455 | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 | 42456 | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 | 42457 | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 | 42458 | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 | 42459 | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W | 2458 | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 | 42460 | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W | 2459 | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Range Vin1 L1N Under | 2460 | 42461 | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W | 2460 | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 | 42462 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2N Under | 2462 | 42463 | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W | 2462 | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 | 42464 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3N Under | 2464 | 42465 | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W | 2464 | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 | 42466 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L1L2 Under | 2466 | 42467 | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W | 2466 | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 | 42468 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2L3 Under | 2468 | 42469 | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W | 2468 | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 | 42470 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3L1 Under | 2470 | 42471 | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W | 2470 | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 | 42472 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin2 L1N Under | 2472 | 42473 | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W | 2472 | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 | 42474 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2N Under | 2474 | 42475 | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W | 2474 | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 | 42476 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3N Under | 2476 | 42477 | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W | 2476 | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 | 42478 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L1L2 Under | 2478 | 42479 | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W | 2478 | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 | 42480 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2L3 Under | 2480 | 42481 | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W | 2480 | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 | 42482 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3L1 Under | 2482 | 42483 | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W | 2482 | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 | 42484 | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 | 42485 | Voltage Alarm Persistence | Sec | Config | uint16 | R/W | 2484 | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 | 42486 | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R | 2485 | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 | 42487 | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 | 42488 | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R | 2487 | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 | 42489 | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 | 42490 | Real Time Clock MSW |  | Config | uint16 | R/W | 2489 | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 | 42491 | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - | USER CONFIG POINTS 2 | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 | 42602 | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 | 42603 | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 | 42604 | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 | 42605 | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 | 42606 | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 | 42607 | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 | 42608 | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 | 42609 | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 | 42610 | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 | 42611 | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 | 42612 | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 | 42613 | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 | 42614 | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 | 42615 | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 | 42616 | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 | 42617 | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 | 42618 | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 | 42619 | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 | 42620 | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 | 42621 | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 | 42622 | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 | 42623 | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 | 42624 | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 | 42625 | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 | 42626 | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 | 42627 | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 | 42628 | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 | 42629 | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 | 42630 | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 | 42631 | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 | 42632 | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 | 42633 | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 | 42634 | BACnet Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | 2634 | 42635 | BACnet Description 1 | [8 empty] | 2 Char |  | ALL
BACnet Description 2 | 2635 | 42636 | BACnet Description 2 | [8 empty] | 2 Char |  | ALL
BACnet Description 3 | 2636 | 42637 | BACnet Description 3 | [8 empty] | 2 Char |  | ALL
BACnet Description 4 | 2637 | 42638 | BACnet Description 4 | [8 empty] | 2 Char |  | ALL
BACnet Description 5 | 2638 | 42639 | BACnet Description 5 | [8 empty] | 2 Char |  | ALL
BACnet Description 6 | 2639 | 42640 | BACnet Description 6 | [8 empty] | 2 Char |  | ALL
BACnet Description 7 | 2640 | 42641 | BACnet Description 7 | [8 empty] | 2 Char |  | ALL
BACnet Description 8 | 2641 | 42642 | BACnet Description 8 | [8 empty] | 2 Char |  | ALL
BACnet Description 9 | 2642 | 42643 | BACnet Description 9 | [8 empty] | 2 Char |  | ALL
BACnet Description 10 | 2643 | 42644 | BACnet Description 10 | [8 empty] | 2 Char |  | ALL
BACnet Description 11 | 2644 | 42645 | BACnet Description 11 | [8 empty] | 2 Char |  | ALL
BACnet Description 12 | 2645 | 42646 | BACnet Description 12 | [8 empty] | 2 Char |  | ALL
BACnet Description 13 | 2646 | 42647 | BACnet Description 13 | [8 empty] | 2 Char |  | ALL
BACnet Description 14 | 2647 | 42648 | BACnet Description 14 | [8 empty] | 2 Char |  | ALL
BACnet Description 15 | 2648 | 42649 | BACnet Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
VERIS EMULATION LEGACY REGISTERS | - | - | VERIS EMULATION LEGACY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Veris Emulation Mode | 2200 | 42201 | Set to Veris Emulation Mode |  | Config | uint16 | R/W |  |  |  | system | 0-1 | 1 = Report Slave ID as Veris Model H8036 | ALL
kWh System LSW | 0 | 40001 | kWh System LSW | kWh | Veris | uint32 | R |  |  |  | element |  |  | ALL
kWh System MSW | 1 | 40002 | kWh System MSW | kWh | Veris |  | R |  |  |  | element |  |  | ALL
kW System | 2 | 40003 | kW System | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVAR System | 3 | 40004 | kVAR System | kVAR | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVA System | 4 | 40005 | kVA System | kVA | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF System | 5 | 40006 | Apparent PF System | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts Line to Line Avg | 6 | 40007 | Volts Line to Line Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts Line to Neutral Avg | 7 | 40008 | Volts Line to Neutral Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps System Avg | 8 | 40009 | Amps System Avg | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L1 | 9 | 40010 | kW L1 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L2 | 10 | 40011 | kW L2 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L3 | 11 | 40012 | kW L3 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L1 | 12 | 40013 | Apparent PF L1 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L2 | 13 | 40014 | Apparent PF L2 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L3 | 14 | 40015 | Apparent PF L3 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts L1 to L2 | 15 | 40016 | Volts L1 to L2 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to L3 | 16 | 40017 | Volts L2 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to L3 | 17 | 40018 | Volts L1 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to Neutral | 18 | 40019 | Volts L1 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to Neutral | 19 | 40020 | Volts L2 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L3 to Neutral | 20 | 40021 | Volts L3 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps L1 | 21 | 40022 | Amps L1 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L2 | 22 | 40023 | Amps L2 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L3 | 23 | 40024 | Amps L3 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW System Avg | 24 | 40025 | kW System Avg | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Now | 25 | 40026 | kW Demand Sys Now (was Min) | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Max | 26 | 40027 | kW Demand Sys Max | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL

## I
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS --> | 9
BACNET OBJECT FLOOR --> | 80000
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 | 41002 | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | 41003 | [8 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 | 41004 | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 | 41005 | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 | 41006 | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | 41007 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | 41008 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | 41009 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | 41010 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | 41011 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | 41012 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | 41013 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | 41014 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | 41015 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | 41016 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | 41017 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | 41018 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | 41019 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | 41020 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | 41021 | [8 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 | 41022 | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | 41023 | [8 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | 41024 | [8 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | 41025 | [8 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | 41026 | [8 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | 41027 | [8 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | 41028 | [8 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | 41029 | [8 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | 41030 | [8 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | 41031 | [8 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | 41032 | [8 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | 41033 | [8 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | 41034 | [8 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | 41035 | [8 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | 41036 | [8 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | 41037 | [8 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 | 41038 | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | 41039 | [8 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | 41040 | [8 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | 41041 | [8 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | 41042 | [8 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | 41043 | [8 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | 41044 | [8 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | 41045 | [8 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 | 41046 | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | 41047 | [8 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | 41048 | [8 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | 41049 | [8 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | 41050 | [8 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | 41051 | [8 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | 41052 | [8 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | 41053 | [8 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 | 41054 | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | 41055 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | 41056 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | 41057 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | 41058 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | 41059 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | 41060 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | 41061 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | 41062 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | 41063 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | 41064 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | 41065 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | 41066 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | 41067 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | 41068 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | 41069 | [8 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 | 41070 | Modbus Device Address |  |  | unit16 | R/W | 1069 | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | 41071 | [8 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 | 41072 | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 | 41073 | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 | 41074 | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | 41075 | [8 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | 41076 | [8 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | 41077 | [8 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 | 41078 | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 | 41079 | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 | 41080 | IP Address |  |  | string(8) | R/W | 1079 | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | 41081 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | 41082 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | 41083 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | 41084 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | 41085 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | 41086 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | 41087 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 | 41088 | Netmask |  |  | string(8) | R/W | 1087 | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | 41089 | [8 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | 41090 | [8 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | 41091 | [8 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | 41092 | [8 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | 41093 | [8 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | 41094 | [8 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | 41095 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 | 41096 | Gateway |  |  | string(8) | R/W | 1095 | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | 41097 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | 41098 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | 41099 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | 41100 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | 41101 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | 41102 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | 41103 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 | 41104 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | 41105 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | 41106 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | 41107 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | 41108 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | 41109 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | 41110 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | 41111 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 | 41112 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | 41113 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | 41114 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | 41115 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | 41116 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | 41117 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | 41118 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | 41119 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 | 41120 | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | 41121 | [8 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | 41122 | [8 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | 41123 | [8 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 | 41124 | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | 41125 | [9 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 | 41126 | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 | 41127 | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 | 41128 | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | 41129 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | 41130 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | 41131 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 | 41132 | Interface baud rate in bits per second |  |  | uint32 | R/W | 1131 | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | 41133 | [8 empty] | system |  |  | ALL
SERIAL BITS | 1133 | 41134 | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 | 41135 | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 | 41136 | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 | 41137 | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 | 41138 | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 | 41139 | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 | 41140 | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 | 41141 | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 | 41142 | Current Avg Element | A | Metrology | float32 | R | 81141 | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | 41143 | [8 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 | 41144 | Current CH1 (A) | A | Metrology | float32 | R | 81143 | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | 41145 | [8 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 | 41146 | Current CH2 (B) | A | Metrology | float32 | R | 81145 | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | 41147 | [8 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 | 41148 | Current CH3 (C) | A | Metrology | float32 | R | 81147 | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | 41149 | [8 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 | 41150 | Voltage L to N Avg Element | V | Metrology | float32 | R | 81149 | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | 41151 | [8 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 | 41152 | Voltage L1 to N (AN) | V | Metrology | float32 | R | 81151 | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | 41153 | [8 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 | 41154 | Voltage L2 to N (BN) | V | Metrology | float32 | R | 81153 | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | 41155 | [8 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 | 41156 | Voltage L3 to N (CN) | V | Metrology | float32 | R | 81155 | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | 41157 | [8 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 | 41158 | Voltage L to L Avg Element | V | Metrology | float32 | R | 81157 | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | 41159 | [8 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 | 41160 | Voltage L1 to L2 (AB) | V | Metrology | float32 | R | 81159 | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | 41161 | [8 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 | 41162 | Voltage L2 to L3 (BC) | V | Metrology | float32 | R | 81161 | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | 41163 | [8 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 | 41164 | Voltage L3 to L1 (CA) | V | Metrology | float32 | R | 81163 | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | 41165 | [8 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 | 41166 | Line Frequency | Hz | Metrology | float32 | R | 81165 | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | 41167 | [8 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 | 41168 | Power Sum Element | kW | Metrology | float32 | R | 81167 | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | 41169 | [8 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 | 41170 | Power CH1 (A) | kW | Metrology | float32 | R | 81169 | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | 41171 | [8 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 | 41172 | Power CH2 (B) | kW | Metrology | float32 | R | 81171 | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | 41173 | [8 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 | 41174 | Power CH3 (C) | kW | Metrology | float32 | R | 81173 | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | 41175 | [8 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 | 41176 | VA Sum Element | kVA | Metrology | float32 | R | 81175 | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | 41177 | [8 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 | 41178 | VA CH1 (A) | kVA | Metrology | float32 | R | 81177 | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | 41179 | [8 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 | 41180 | VA CH2 (B) | kVA | Metrology | float32 | R | 81179 | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | 41181 | [8 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 | 41182 | VA CH3 (C) | kVA | Metrology | float32 | R | 81181 | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | 41183 | [8 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 | 41184 | VAR Sum Element | kVAr | Metrology | float32 | R | 81183 | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | 41185 | [8 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 | 41186 | VAR CH1 (A) | kVAr | Metrology | float32 | R | 81185 | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | 41187 | [8 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 | 41188 | VAR CH2 (B) | kVAr | Metrology | float32 | R | 81187 | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | 41189 | [8 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 | 41190 | VAR CH3 (C) | kVAr | Metrology | float32 | R | 81189 | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | 41191 | [8 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 | 41192 | Apparent PF Avg Element | PF | Metrology | float32 | R | 81191 | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | 41193 | [8 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 | 41194 | Apparent PF CH1 (A) | PF | Metrology | float32 | R | 81193 | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | 41195 | [8 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 | 41196 | Apparent PF CH2 (B) | PF | Metrology | float32 | R | 81195 | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | 41197 | [8 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 | 41198 | Apparent PF CH3 ( C) | PF | Metrology | float32 | R | 81197 | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | 41199 | [8 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 | 41200 | Exported Energy Sum Element | kWh | Metrology | float32 | R | 81199 | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | 41201 | [8 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 | 41202 | Exported Energy CH1 (A) | kWh | Metrology | float32 | R | 81201 | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | 41203 | [8 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 | 41204 | Exported Energy CH2 (B) | kWh | Metrology | float32 | R | 81203 | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | 41205 | [8 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 | 41206 | Exported Energy CH3 (C) | kWh | Metrology | float32 | R | 81205 | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | 41207 | [8 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 | 41208 | Imported Energy Sum Element | kWh | Metrology | float32 | R | 81207 | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | 41209 | [8 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 | 41210 | Imported Energy CH1 (A) | kWh | Metrology | float32 | R | 81209 | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | 41211 | [8 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 | 41212 | Imported Energy CH2 (B) | kWh | Metrology | float32 | R | 81211 | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | 41213 | [8 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 | 41214 | Imported Energy CH3 (C) | kWh | Metrology | float32 | R | 81213 | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | 41215 | [8 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 | 41216 | Exported VAh Sum Element | kVAh | Metrology | float32 | R | 81215 | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | 41217 | [8 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 | 41218 | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R | 81217 | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | 41219 | [8 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 | 41220 | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R | 81219 | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | 41221 | [8 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 | 41222 | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R | 81221 | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | 41223 | [8 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 | 41224 | Imported VAh Sum Element | kVAh | Metrology | float32 | R | 81223 | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | 41225 | [8 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 | 41226 | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R | 81225 | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | 41227 | [8 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 | 41228 | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R | 81227 | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | 41229 | [8 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 | 41230 | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R | 81229 | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | 41231 | [8 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 | 41232 | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R | 81231 | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | 41233 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 | 41234 | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R | 81233 | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | 41235 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 | 41236 | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R | 81235 | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | 41237 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 | 41238 | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R | 81237 | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | 41239 | [8 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 | 41240 | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R | 81239 | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | 41241 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 | 41242 | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R | 81241 | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | 41243 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 | 41244 | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R | 81243 | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | 41245 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 | 41246 | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R | 81245 | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | 41247 | [8 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 | 41248 | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R | 81247 | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | 41249 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 | 41250 | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R | 81249 | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | 41251 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 | 41252 | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R | 81251 | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | 41253 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 | 41254 | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R | 81253 | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | 41255 | [8 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 | 41256 | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R | 81255 | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | 41257 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 | 41258 | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R | 81257 | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | 41259 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 | 41260 | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R | 81259 | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | 41261 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 | 41262 | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R | 81261 | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | 41263 | [8 empty] | element |  |  | ALL
Events MSW | 1263 | 41264 | Events MSW |  |  | bitfield32 | R | 1263 | AI | Events | system |  |  | ALL
Events LSW | 1264 | 41265 | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 | 41266 | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 | 41267 | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
FACTORY REGISTERS | - | - | FACTORY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Factory Unlock Register | 2000 | 42001 | Factory Unlock Register |  | Factory | unit16 | R/W |  |  |  | system |  | Reserved | ALL
Factory Reset | 2001 | 42002 | Factory Reset |  | Factory | unit16 | R/W |  |  |  | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
OEM Vendor ID | 2002 | 42003 | OEM Vendor ID |  | Factory | unit16 | R |  |  |  | system |  | Reserved | ALL
FACTORY_CONFIG | 2003 | 42004 | Factory Config |  | Factory | unit16 | R |  |  |  | system | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable | ALL
USER COMMAND POINTS | - | - | USER COMMAND POINTS | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 | 42101 | Reset (software) processor |  | User | unit16 | W | 2100 | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 | 42102 | Clear all accumulated measurements (CAM) |  | User | unit16 | W | 2101 | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 | 42103 | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W | 82102 | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 | 42104 | Clear Peak Demand Element |  | User | unit16 | W | 82103 | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 | 42105 | Clear Peak Demand All |  | User | unit16 | W | 2104 | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 | 42106 | Reset to User Defaults |  | User | unit16 | W | 2105 | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - | USER CONFIG POINTS | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 | 42202 | Sliding or Fixed |  | Config | enum16 | R | 2201 | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 | 42203 | Demand Window | Min | Config | uint16 | R | 2202 | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 | 42204 | Volt Multiplier VINPUT1 |  | Config | float32 | R/W | 2203 | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | 42205 | [8 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 | 42206 | Volt Multiplier VINPUT2 |  | Config | float32 | R/W | 2205 | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | 42207 | [8 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 | 42208 | Service Type |  | Config | enum16 | R/W | 82207 | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 | 42209 | Snap MV Threshold | PER | Config | float32 | R/W | 2208 | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | 42210 | [8 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 | 42211 | Snap Rog Threshold | PER | Config | float32 | R/W | 2210 | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | 42212 | [8 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 | 42213 | Snap Volt Threshold | V | Config | float32 | R/W | 2212 | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | 42214 | [8 empty] | system |  |  | ALL
Communications Mode | 2214 | 42215 | Communications Mode |  | Config |  |  | 2214 | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 | 42216 | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W | 2215 | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | 42217 | [8 empty] | system |  |  | ALL
Voltage Input Element | 2217 | 42218 | Element Voltage Input |  | Config | enum16 | R/W | 82217 | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 | 42219 | CT1 RANGE | A | Config | float32 | R/W | 82218 | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | 42220 | [8 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 | 42221 | Voltage Reference for CT1 |  | Config | enum16 | R/W | 82220 | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 | 42222 | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W | 82221 | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | 42223 | [8 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 | 42224 | CT1 TYPE |  | Config | enum16 | R/W | 82223 | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 | 42225 | CT1 PHASE SHIFT | Deg | Config | float32 | R/W | 82224 | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | 42226 | [8 empty] | element |  |  | ALL
CH1 CT Sign | 2226 | 42227 | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W | 82226 | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 | 42228 | CT2 RANGE | A | Config | float32 | R/W | 82227 | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | 42229 | [8 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 | 42230 | Voltage Reference for CT2 |  | Config | enum16 | R/W | 82229 | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 | 42231 | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W | 82230 | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | 42232 | [8 empty] | element | >0 |  | ALL
CH2 CT type | 2232 | 42233 | CT2 TYPE |  | Config | enum16 | R/W | 82232 | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 | 42234 | CT2 PHASE SHIFT | Deg | Config | float32 | R/W | 82233 | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | 42235 | [8 empty] | element |  |  | ALL
CH2 CT Sign | 2235 | 42236 | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W | 82235 | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 | 42237 | CT3 INTEGER | A | Config | float32 | R/W | 82236 | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | 42238 | [8 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 | 42239 | Voltage Reference for CT3 |  | Config | enum16 | R/W | 82238 | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 | 42240 | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W | 82239 | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | 42241 | [8 empty] | element | >0 |  | ALL
CH3 CT type | 2241 | 42242 | CT3 TYPE |  | Config | enum16 | R/W | 82241 | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 | 42243 | CT3 PHASE SHIFT | Deg | Config | float32 | R/W | 82242 | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | 42244 | [8 empty] | element |  |  | ALL
CH3 CT Sign | 2244 | 42245 | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W | 82244 | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 | 42246 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 | 42247 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 | 42248 | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 | 42249 | PF Sign Convention |  | Config | uint16 | R/W | 2248 | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 | 42250 | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 | 42251 | BACnet UDP Port |  | Config | uint16 | R/W | 2250 | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 | 42252 | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 | 42253 | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | 42254 | [8 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 | 42261 | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | 42262 | [11 empty] | ALL
BACnet Max Info Frames | 2262 | 42263 | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 | 42264 | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 | 42265 | BBMD IP Address |  | Config | string(16) | R/W | 2264 | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | 42266 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | 42267 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | 42268 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | 42269 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | 42270 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | 42271 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | 42272 | [9 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 | 42273 | LCD/WebApp Read Password |  | Config | uint16 | R/W | 2272 | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 | 42274 | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 | 42275 | Customer Line frequency |  | Config | float | R/W | 2274 | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | 42276 | [10 empty] | Reserved | ALL
Communications Interface Configured | 2276 | 42277 | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 | 42278 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 | 42279 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 | 42280 | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 | 42281 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 | 42282 | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 | 42283 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 | 42284 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 | 42285 | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 | 42286 | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 | 42287 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 | 42288 | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 | 42289 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 | 42290 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 | 42291 | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 | 42292 | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | 42293 | [11 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 | 42294 | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | 42295 | [11 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 | 42296 | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 | 42297 | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - | METROLOGY POINTS | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 | 42301 | Displacement PF Avg Element | dPF | Metrology | float32 | R | 82300 | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | 42302 | [11 empty] | ALL
Displacement PF CH1 (MSW) | 2302 | 42303 | Displacement PF CH1 (A) | dPF | Metrology | float32 | R | 82302 | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | 42304 | [11 empty] | ALL
Displacement PF CH2 (MSW) | 2304 | 42305 | Displacement PF CH2 (B) | dPF | Metrology | float32 | R | 82304 | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | 42306 | [11 empty] | ALL
Displacement PF CH3 (MSW) | 2306 | 42307 | Displacement PF CH3 (C) | dPF | Metrology | float32 | R | 82306 | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | 42308 | [11 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 | 42309 | Avg Apparent PF Element | aPF | Metrology | float32 | R | 82308 | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | 42310 | [11 empty] | ALL
Apparent PF CH1 (MSW) | 2310 | 42311 | Apparent PF CH1 (A) | aPF | Metrology | float32 | R | 82310 | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | 42312 | [11 empty] | ALL
Apparent PF CH2 (MSW) | 2312 | 42313 | Apparent PF CH2 (B) | aPF | Metrology | float32 | R | 82312 | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | 42314 | [11 empty] | ALL
Apparent PF CH3 (MSW) | 2314 | 42315 | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R | 82314 | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | 42316 | [11 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 | 42317 | Distortion PF Avg Element | tPF | Metrology | float32 | R | 82316 | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | 42318 | [11 empty] | ALL
Distortion PF CH1 (MSW) | 2318 | 42319 | Distortion PF CH1 (A) | tPF | Metrology | float32 | R | 82318 | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | 42320 | [11 empty] | ALL
Distortion PF CH2 (MSW) | 2320 | 42321 | Distortion PF CH2 (B) | tPF | Metrology | float32 | R | 82320 | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | 42322 | [11 empty] | ALL
Distortion PF CH3 (MSW) | 2322 | 42323 | Distortion PF CH3 (C) | tPF | Metrology | float32 | R | 82322 | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | 42324 | [11 empty] | ALL
THD Avg Element (MSW) | 2324 | 42325 | THD Avg Element | % | Metrology | float32 | R | 82324 | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | 42326 | [11 empty] | ALL
THD CH1 (MSW) | 2326 | 42327 | THD CH1 (A) | % | Metrology | float32 | R | 82326 | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | 42328 | [11 empty] | ALL
THD CH2 (MSW) | 2328 | 42329 | THD CH2 (B) | % | Metrology | float32 | R | 82328 | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | 42330 | [11 empty] | ALL
THD CH3 (MSW) | 2330 | 42331 | THD CH3 (C) | % | Metrology | float32 | R | 82330 | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | 42332 | [11 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 | 42333 | Power Demand Max Interval Element | kW | Metrology | float32 | R | 82332 | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | 42334 | [11 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 | 42335 | Power Demand This Interval Element | kW | Metrology | float32 | R | 82334 | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | 42336 | [11 empty] | ALL
VA Peak Demand Element (MSW) | 2336 | 42337 | VA Demand Max Interval Element | kVA | Metrology | float32 | R | 82336 | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | 42338 | [11 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 | 42339 | VA Demand This Interval Element | kVA | Metrology | float32 | R | 82338 | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | 42340 | [11 empty] | ALL
Not Used | 2340 | 42341 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 | 42342 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 | 42343 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 | 42344 | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 | 42345 | Energy Net Sum Element | kWh | Metrology | float32 | R | 82344 | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | 42346 | [8 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 | 42347 | Energy Net CH1 | kWh | Metrology | float32 | R | 82346 | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | 42348 | [8 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 | 42349 | Energy Net CH2 | kWh | Metrology | float32 | R | 82348 | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | 42350 | [8 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 | 42351 | Energy Net CH3 | kWh | Metrology | float32 | R | 82350 | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | 42352 | [8 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 | 42353 | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R | 82352 | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | 42354 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 | 42355 | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R | 82354 | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | 42356 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 | 42357 | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R | 82356 | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | 42358 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 | 42359 | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R | 82358 | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | 42360 | [8 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 | 42361 | VARh Net Sum Element | kVArh | Metrology | float32 | R | 82360 | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | 42362 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 | 42363 | VARh Net CH1 | kVArh | Metrology | float32 | R | 82362 | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | 42364 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 | 42365 | VARh Net CH2 | kVArh | Metrology | float32 | R | 82364 | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | 42366 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 | 42367 | VARh Net CH3 | kVArh | Metrology | float32 | R | 82366 | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | 42368 | [8 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 | 42369 | Time Since Reset MSW | Sec | Metrology | uint32 |  | 2368 | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 | 42370 | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 | 42371 | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 | 42372 | CH1 Angle | Deg | Metrology | float32 | R | 82371 | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | 42373 | [8 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 | 42374 | CH2 Angle | Deg | Metrology | float32 | R | 82373 | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | 42375 | [8 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 | 42376 | CH3 Angle | Deg | Metrology | float32 | R | 82375 | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | 42377 | [11 empty] | ALL
Phase Chek System Status | 2377 | 42378 | System Phase Check Status |  | Metrology | bitfield16 | R | 2377 | BV | Phase Check System Status | system | 0,1 | 0 (All Channels OK), 1(Somewhere a channel is reading a dPF < 0.55), check register 2378 for each Element | ALL
Phase Chek Element Status | 2378 | 42379 | Element Phase Check Status |  | Metrology | bitfield16 | R | 82378 | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 | 42380 | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 | 42381 | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 | 42382 | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 | 42392 | Element Angle |  | Metrology | float | R | 82391 | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | 42393 | [11 empty] | ALL
PULSE INPUTS | - | - | PULSE INPUTS | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 | 42401 | Pulse Input 1 Enable |  | Config | uint16 | R/W | 2400 | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 | 42402 | Pulse Input 1 Scale Factor |  | Config | float32 | R/W | 2401 | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 | 42403 |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 | 42404 | Pulse Input 1 Units |  | Config | string(4) | R/W | 2403 | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 | 42405 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 | 42406 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 | 42407 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 | 42408 | Pulse Input 1 Accumulator |  | Metrology | float32 | R | 2407 | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | 42409 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 | 42410 | Pulse Input 1 Accumulator Clear |  | User | unit16 | W | 2409 | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 | 42411 | Pulse Input 2 Enable |  | Config | uint16 | R/W | 2410 | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 | 42412 | Pulse Input 2 Scale Factor |  | Config | float32 | R/W | 2411 | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | 42413 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 | 42414 | Pulse Input 2 Units |  | Config | string(4) | R/W | 2413 | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 | 42415 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 | 42416 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 | 42417 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 | 42418 | Pulse Input 2 Accumulator |  | Metrology | float32 | R | 2417 | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | 42419 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 | 42420 | Pulse Input 2 Accumulator Clear |  | User | unit16 | W | 2419 | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 | 42421 | Pulse Input 3 Enable |  | Config | uint16 | R/W | 2420 | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 | 42422 | Pulse Input 3 Scale Factor |  | Config | float32 | R/W | 2421 | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | 42423 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 | 42424 | Pulse Input 3 Units |  | Config | string(4) | R/W | 2423 | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 | 42425 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 | 42426 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 | 42427 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 | 42428 | Pulse Input 3 Accumulator |  | Metrology | float32 | R | 2427 | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | 42429 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 | 42430 | Pulse Input 3 Accumulator Clear |  | User |  | W | 2429 | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 | 42431 | Pulse Input 4 Enable |  | Config | uint16 | R/W | 2430 | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 | 42432 | Pulse Input 4 Scale Factor |  | Config | float32 | R/W | 2431 | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | 42433 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 | 42434 | Pulse Input 4 Units |  | Config | string(4) | R/W | 2433 | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 | 42435 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 | 42436 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 | 42437 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 | 42438 | Pulse Input 4 Accumulator |  | Metrology | float32 | R | 2437 | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | 42439 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 | 42440 | Pulse Input 4 Accumulator Clear |  | User | unit16 | W | 2439 | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - | ALARMS | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 | 42452 | State of Alarm |  | Metrology | uint16 | R/W | 2451 | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 | 42453 | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 | 42454 | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 | 42455 | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 | 42456 | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 | 42457 | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 | 42458 | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 | 42459 | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W | 2458 | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 | 42460 | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W | 2459 | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Range Vin1 L1N Under | 2460 | 42461 | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W | 2460 | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 | 42462 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2N Under | 2462 | 42463 | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W | 2462 | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 | 42464 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3N Under | 2464 | 42465 | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W | 2464 | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 | 42466 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L1L2 Under | 2466 | 42467 | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W | 2466 | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 | 42468 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2L3 Under | 2468 | 42469 | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W | 2468 | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 | 42470 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3L1 Under | 2470 | 42471 | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W | 2470 | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 | 42472 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin2 L1N Under | 2472 | 42473 | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W | 2472 | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 | 42474 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2N Under | 2474 | 42475 | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W | 2474 | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 | 42476 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3N Under | 2476 | 42477 | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W | 2476 | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 | 42478 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L1L2 Under | 2478 | 42479 | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W | 2478 | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 | 42480 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2L3 Under | 2480 | 42481 | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W | 2480 | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 | 42482 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3L1 Under | 2482 | 42483 | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W | 2482 | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 | 42484 | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 | 42485 | Voltage Alarm Persistence | Sec | Config | uint16 | R/W | 2484 | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 | 42486 | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R | 2485 | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 | 42487 | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 | 42488 | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R | 2487 | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 | 42489 | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 | 42490 | Real Time Clock MSW |  | Config | uint16 | R/W | 2489 | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 | 42491 | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - | USER CONFIG POINTS 2 | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 | 42602 | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 | 42603 | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 | 42604 | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 | 42605 | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 | 42606 | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 | 42607 | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 | 42608 | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 | 42609 | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 | 42610 | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 | 42611 | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 | 42612 | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 | 42613 | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 | 42614 | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 | 42615 | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 | 42616 | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 | 42617 | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 | 42618 | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 | 42619 | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 | 42620 | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 | 42621 | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 | 42622 | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 | 42623 | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 | 42624 | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 | 42625 | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 | 42626 | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 | 42627 | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 | 42628 | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 | 42629 | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 | 42630 | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 | 42631 | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 | 42632 | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 | 42633 | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 | 42634 | BACnet Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | 2634 | 42635 | BACnet Description 1 | [8 empty] | 2 Char |  | ALL
BACnet Description 2 | 2635 | 42636 | BACnet Description 2 | [8 empty] | 2 Char |  | ALL
BACnet Description 3 | 2636 | 42637 | BACnet Description 3 | [8 empty] | 2 Char |  | ALL
BACnet Description 4 | 2637 | 42638 | BACnet Description 4 | [8 empty] | 2 Char |  | ALL
BACnet Description 5 | 2638 | 42639 | BACnet Description 5 | [8 empty] | 2 Char |  | ALL
BACnet Description 6 | 2639 | 42640 | BACnet Description 6 | [8 empty] | 2 Char |  | ALL
BACnet Description 7 | 2640 | 42641 | BACnet Description 7 | [8 empty] | 2 Char |  | ALL
BACnet Description 8 | 2641 | 42642 | BACnet Description 8 | [8 empty] | 2 Char |  | ALL
BACnet Description 9 | 2642 | 42643 | BACnet Description 9 | [8 empty] | 2 Char |  | ALL
BACnet Description 10 | 2643 | 42644 | BACnet Description 10 | [8 empty] | 2 Char |  | ALL
BACnet Description 11 | 2644 | 42645 | BACnet Description 11 | [8 empty] | 2 Char |  | ALL
BACnet Description 12 | 2645 | 42646 | BACnet Description 12 | [8 empty] | 2 Char |  | ALL
BACnet Description 13 | 2646 | 42647 | BACnet Description 13 | [8 empty] | 2 Char |  | ALL
BACnet Description 14 | 2647 | 42648 | BACnet Description 14 | [8 empty] | 2 Char |  | ALL
BACnet Description 15 | 2648 | 42649 | BACnet Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
VERIS EMULATION LEGACY REGISTERS | - | - | VERIS EMULATION LEGACY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Veris Emulation Mode | 2200 | 42201 | Set to Veris Emulation Mode |  | Config | uint16 | R/W |  |  |  | system | 0-1 | 1 = Report Slave ID as Veris Model H8036 | ALL
kWh System LSW | 0 | 40001 | kWh System LSW | kWh | Veris | uint32 | R |  |  |  | element |  |  | ALL
kWh System MSW | 1 | 40002 | kWh System MSW | kWh | Veris |  | R |  |  |  | element |  |  | ALL
kW System | 2 | 40003 | kW System | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVAR System | 3 | 40004 | kVAR System | kVAR | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVA System | 4 | 40005 | kVA System | kVA | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF System | 5 | 40006 | Apparent PF System | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts Line to Line Avg | 6 | 40007 | Volts Line to Line Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts Line to Neutral Avg | 7 | 40008 | Volts Line to Neutral Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps System Avg | 8 | 40009 | Amps System Avg | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L1 | 9 | 40010 | kW L1 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L2 | 10 | 40011 | kW L2 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L3 | 11 | 40012 | kW L3 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L1 | 12 | 40013 | Apparent PF L1 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L2 | 13 | 40014 | Apparent PF L2 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L3 | 14 | 40015 | Apparent PF L3 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts L1 to L2 | 15 | 40016 | Volts L1 to L2 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to L3 | 16 | 40017 | Volts L2 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to L3 | 17 | 40018 | Volts L1 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to Neutral | 18 | 40019 | Volts L1 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to Neutral | 19 | 40020 | Volts L2 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L3 to Neutral | 20 | 40021 | Volts L3 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps L1 | 21 | 40022 | Amps L1 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L2 | 22 | 40023 | Amps L2 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L3 | 23 | 40024 | Amps L3 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW System Avg | 24 | 40025 | kW System Avg | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Now | 25 | 40026 | kW Demand Sys Now (was Min) | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Max | 26 | 40027 | kW Demand Sys Max | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL

## J
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS --> | 10
BACNET OBJECT FLOOR --> | 90000
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 | 41002 | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | 41003 | [8 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 | 41004 | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 | 41005 | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 | 41006 | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | 41007 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | 41008 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | 41009 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | 41010 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | 41011 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | 41012 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | 41013 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | 41014 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | 41015 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | 41016 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | 41017 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | 41018 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | 41019 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | 41020 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | 41021 | [8 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 | 41022 | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | 41023 | [8 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | 41024 | [8 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | 41025 | [8 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | 41026 | [8 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | 41027 | [8 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | 41028 | [8 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | 41029 | [8 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | 41030 | [8 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | 41031 | [8 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | 41032 | [8 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | 41033 | [8 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | 41034 | [8 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | 41035 | [8 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | 41036 | [8 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | 41037 | [8 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 | 41038 | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | 41039 | [8 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | 41040 | [8 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | 41041 | [8 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | 41042 | [8 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | 41043 | [8 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | 41044 | [8 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | 41045 | [8 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 | 41046 | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | 41047 | [8 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | 41048 | [8 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | 41049 | [8 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | 41050 | [8 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | 41051 | [8 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | 41052 | [8 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | 41053 | [8 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 | 41054 | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | 41055 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | 41056 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | 41057 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | 41058 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | 41059 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | 41060 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | 41061 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | 41062 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | 41063 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | 41064 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | 41065 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | 41066 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | 41067 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | 41068 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | 41069 | [8 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 | 41070 | Modbus Device Address |  |  | unit16 | R/W | 1069 | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | 41071 | [8 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 | 41072 | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 | 41073 | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 | 41074 | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | 41075 | [8 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | 41076 | [8 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | 41077 | [8 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 | 41078 | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 | 41079 | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 | 41080 | IP Address |  |  | string(8) | R/W | 1079 | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | 41081 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | 41082 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | 41083 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | 41084 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | 41085 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | 41086 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | 41087 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 | 41088 | Netmask |  |  | string(8) | R/W | 1087 | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | 41089 | [8 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | 41090 | [8 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | 41091 | [8 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | 41092 | [8 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | 41093 | [8 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | 41094 | [8 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | 41095 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 | 41096 | Gateway |  |  | string(8) | R/W | 1095 | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | 41097 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | 41098 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | 41099 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | 41100 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | 41101 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | 41102 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | 41103 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 | 41104 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | 41105 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | 41106 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | 41107 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | 41108 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | 41109 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | 41110 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | 41111 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 | 41112 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | 41113 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | 41114 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | 41115 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | 41116 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | 41117 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | 41118 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | 41119 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 | 41120 | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | 41121 | [8 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | 41122 | [8 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | 41123 | [8 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 | 41124 | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | 41125 | [9 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 | 41126 | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 | 41127 | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 | 41128 | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | 41129 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | 41130 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | 41131 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 | 41132 | Interface baud rate in bits per second |  |  | uint32 | R/W | 1131 | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | 41133 | [8 empty] | system |  |  | ALL
SERIAL BITS | 1133 | 41134 | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 | 41135 | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 | 41136 | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 | 41137 | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 | 41138 | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 | 41139 | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 | 41140 | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 | 41141 | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 | 41142 | Current Avg Element | A | Metrology | float32 | R | 91141 | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | 41143 | [8 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 | 41144 | Current CH1 (A) | A | Metrology | float32 | R | 91143 | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | 41145 | [8 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 | 41146 | Current CH2 (B) | A | Metrology | float32 | R | 91145 | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | 41147 | [8 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 | 41148 | Current CH3 (C) | A | Metrology | float32 | R | 91147 | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | 41149 | [8 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 | 41150 | Voltage L to N Avg Element | V | Metrology | float32 | R | 91149 | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | 41151 | [8 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 | 41152 | Voltage L1 to N (AN) | V | Metrology | float32 | R | 91151 | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | 41153 | [8 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 | 41154 | Voltage L2 to N (BN) | V | Metrology | float32 | R | 91153 | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | 41155 | [8 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 | 41156 | Voltage L3 to N (CN) | V | Metrology | float32 | R | 91155 | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | 41157 | [8 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 | 41158 | Voltage L to L Avg Element | V | Metrology | float32 | R | 91157 | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | 41159 | [8 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 | 41160 | Voltage L1 to L2 (AB) | V | Metrology | float32 | R | 91159 | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | 41161 | [8 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 | 41162 | Voltage L2 to L3 (BC) | V | Metrology | float32 | R | 91161 | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | 41163 | [8 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 | 41164 | Voltage L3 to L1 (CA) | V | Metrology | float32 | R | 91163 | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | 41165 | [8 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 | 41166 | Line Frequency | Hz | Metrology | float32 | R | 91165 | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | 41167 | [8 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 | 41168 | Power Sum Element | kW | Metrology | float32 | R | 91167 | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | 41169 | [8 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 | 41170 | Power CH1 (A) | kW | Metrology | float32 | R | 91169 | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | 41171 | [8 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 | 41172 | Power CH2 (B) | kW | Metrology | float32 | R | 91171 | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | 41173 | [8 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 | 41174 | Power CH3 (C) | kW | Metrology | float32 | R | 91173 | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | 41175 | [8 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 | 41176 | VA Sum Element | kVA | Metrology | float32 | R | 91175 | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | 41177 | [8 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 | 41178 | VA CH1 (A) | kVA | Metrology | float32 | R | 91177 | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | 41179 | [8 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 | 41180 | VA CH2 (B) | kVA | Metrology | float32 | R | 91179 | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | 41181 | [8 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 | 41182 | VA CH3 (C) | kVA | Metrology | float32 | R | 91181 | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | 41183 | [8 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 | 41184 | VAR Sum Element | kVAr | Metrology | float32 | R | 91183 | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | 41185 | [8 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 | 41186 | VAR CH1 (A) | kVAr | Metrology | float32 | R | 91185 | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | 41187 | [8 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 | 41188 | VAR CH2 (B) | kVAr | Metrology | float32 | R | 91187 | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | 41189 | [8 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 | 41190 | VAR CH3 (C) | kVAr | Metrology | float32 | R | 91189 | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | 41191 | [8 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 | 41192 | Apparent PF Avg Element | PF | Metrology | float32 | R | 91191 | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | 41193 | [8 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 | 41194 | Apparent PF CH1 (A) | PF | Metrology | float32 | R | 91193 | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | 41195 | [8 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 | 41196 | Apparent PF CH2 (B) | PF | Metrology | float32 | R | 91195 | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | 41197 | [8 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 | 41198 | Apparent PF CH3 ( C) | PF | Metrology | float32 | R | 91197 | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | 41199 | [8 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 | 41200 | Exported Energy Sum Element | kWh | Metrology | float32 | R | 91199 | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | 41201 | [8 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 | 41202 | Exported Energy CH1 (A) | kWh | Metrology | float32 | R | 91201 | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | 41203 | [8 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 | 41204 | Exported Energy CH2 (B) | kWh | Metrology | float32 | R | 91203 | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | 41205 | [8 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 | 41206 | Exported Energy CH3 (C) | kWh | Metrology | float32 | R | 91205 | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | 41207 | [8 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 | 41208 | Imported Energy Sum Element | kWh | Metrology | float32 | R | 91207 | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | 41209 | [8 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 | 41210 | Imported Energy CH1 (A) | kWh | Metrology | float32 | R | 91209 | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | 41211 | [8 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 | 41212 | Imported Energy CH2 (B) | kWh | Metrology | float32 | R | 91211 | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | 41213 | [8 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 | 41214 | Imported Energy CH3 (C) | kWh | Metrology | float32 | R | 91213 | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | 41215 | [8 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 | 41216 | Exported VAh Sum Element | kVAh | Metrology | float32 | R | 91215 | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | 41217 | [8 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 | 41218 | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R | 91217 | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | 41219 | [8 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 | 41220 | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R | 91219 | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | 41221 | [8 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 | 41222 | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R | 91221 | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | 41223 | [8 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 | 41224 | Imported VAh Sum Element | kVAh | Metrology | float32 | R | 91223 | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | 41225 | [8 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 | 41226 | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R | 91225 | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | 41227 | [8 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 | 41228 | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R | 91227 | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | 41229 | [8 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 | 41230 | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R | 91229 | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | 41231 | [8 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 | 41232 | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R | 91231 | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | 41233 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 | 41234 | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R | 91233 | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | 41235 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 | 41236 | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R | 91235 | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | 41237 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 | 41238 | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R | 91237 | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | 41239 | [8 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 | 41240 | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R | 91239 | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | 41241 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 | 41242 | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R | 91241 | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | 41243 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 | 41244 | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R | 91243 | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | 41245 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 | 41246 | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R | 91245 | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | 41247 | [8 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 | 41248 | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R | 91247 | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | 41249 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 | 41250 | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R | 91249 | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | 41251 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 | 41252 | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R | 91251 | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | 41253 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 | 41254 | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R | 91253 | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | 41255 | [8 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 | 41256 | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R | 91255 | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | 41257 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 | 41258 | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R | 91257 | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | 41259 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 | 41260 | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R | 91259 | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | 41261 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 | 41262 | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R | 91261 | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | 41263 | [8 empty] | element |  |  | ALL
Events MSW | 1263 | 41264 | Events MSW |  |  | bitfield32 | R | 1263 | AI | Events | system |  |  | ALL
Events LSW | 1264 | 41265 | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 | 41266 | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 | 41267 | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
FACTORY REGISTERS | - | - | FACTORY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Factory Unlock Register | 2000 | 42001 | Factory Unlock Register |  | Factory | unit16 | R/W |  |  |  | system |  | Reserved | ALL
Factory Reset | 2001 | 42002 | Factory Reset |  | Factory | unit16 | R/W |  |  |  | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
OEM Vendor ID | 2002 | 42003 | OEM Vendor ID |  | Factory | unit16 | R |  |  |  | system |  | Reserved | ALL
FACTORY_CONFIG | 2003 | 42004 | Factory Config |  | Factory | unit16 | R |  |  |  | system | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable | ALL
USER COMMAND POINTS | - | - | USER COMMAND POINTS | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 | 42101 | Reset (software) processor |  | User | unit16 | W | 2100 | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 | 42102 | Clear all accumulated measurements (CAM) |  | User | unit16 | W | 2101 | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 | 42103 | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W | 92102 | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 | 42104 | Clear Peak Demand Element |  | User | unit16 | W | 92103 | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 | 42105 | Clear Peak Demand All |  | User | unit16 | W | 2104 | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 | 42106 | Reset to User Defaults |  | User | unit16 | W | 2105 | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - | USER CONFIG POINTS | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 | 42202 | Sliding or Fixed |  | Config | enum16 | R | 2201 | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 | 42203 | Demand Window | Min | Config | uint16 | R | 2202 | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 | 42204 | Volt Multiplier VINPUT1 |  | Config | float32 | R/W | 2203 | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | 42205 | [8 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 | 42206 | Volt Multiplier VINPUT2 |  | Config | float32 | R/W | 2205 | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | 42207 | [8 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 | 42208 | Service Type |  | Config | enum16 | R/W | 92207 | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 | 42209 | Snap MV Threshold | PER | Config | float32 | R/W | 2208 | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | 42210 | [8 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 | 42211 | Snap Rog Threshold | PER | Config | float32 | R/W | 2210 | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | 42212 | [8 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 | 42213 | Snap Volt Threshold | V | Config | float32 | R/W | 2212 | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | 42214 | [8 empty] | system |  |  | ALL
Communications Mode | 2214 | 42215 | Communications Mode |  | Config |  |  | 2214 | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 | 42216 | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W | 2215 | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | 42217 | [8 empty] | system |  |  | ALL
Voltage Input Element | 2217 | 42218 | Element Voltage Input |  | Config | enum16 | R/W | 92217 | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 | 42219 | CT1 RANGE | A | Config | float32 | R/W | 92218 | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | 42220 | [8 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 | 42221 | Voltage Reference for CT1 |  | Config | enum16 | R/W | 92220 | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 | 42222 | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W | 92221 | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | 42223 | [8 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 | 42224 | CT1 TYPE |  | Config | enum16 | R/W | 92223 | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 | 42225 | CT1 PHASE SHIFT | Deg | Config | float32 | R/W | 92224 | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | 42226 | [8 empty] | element |  |  | ALL
CH1 CT Sign | 2226 | 42227 | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W | 92226 | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 | 42228 | CT2 RANGE | A | Config | float32 | R/W | 92227 | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | 42229 | [8 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 | 42230 | Voltage Reference for CT2 |  | Config | enum16 | R/W | 92229 | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 | 42231 | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W | 92230 | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | 42232 | [8 empty] | element | >0 |  | ALL
CH2 CT type | 2232 | 42233 | CT2 TYPE |  | Config | enum16 | R/W | 92232 | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 | 42234 | CT2 PHASE SHIFT | Deg | Config | float32 | R/W | 92233 | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | 42235 | [8 empty] | element |  |  | ALL
CH2 CT Sign | 2235 | 42236 | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W | 92235 | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 | 42237 | CT3 INTEGER | A | Config | float32 | R/W | 92236 | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | 42238 | [8 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 | 42239 | Voltage Reference for CT3 |  | Config | enum16 | R/W | 92238 | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 | 42240 | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W | 92239 | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | 42241 | [8 empty] | element | >0 |  | ALL
CH3 CT type | 2241 | 42242 | CT3 TYPE |  | Config | enum16 | R/W | 92241 | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 | 42243 | CT3 PHASE SHIFT | Deg | Config | float32 | R/W | 92242 | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | 42244 | [8 empty] | element |  |  | ALL
CH3 CT Sign | 2244 | 42245 | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W | 92244 | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 | 42246 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 | 42247 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 | 42248 | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 | 42249 | PF Sign Convention |  | Config | uint16 | R/W | 2248 | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 | 42250 | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 | 42251 | BACnet UDP Port |  | Config | uint16 | R/W | 2250 | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 | 42252 | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 | 42253 | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | 42254 | [8 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 | 42261 | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | 42262 | [11 empty] | ALL
BACnet Max Info Frames | 2262 | 42263 | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 | 42264 | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 | 42265 | BBMD IP Address |  | Config | string(16) | R/W | 2264 | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | 42266 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | 42267 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | 42268 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | 42269 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | 42270 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | 42271 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | 42272 | [9 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 | 42273 | LCD/WebApp Read Password |  | Config | uint16 | R/W | 2272 | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 | 42274 | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 | 42275 | Customer Line frequency |  | Config | float | R/W | 2274 | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | 42276 | [10 empty] | Reserved | ALL
Communications Interface Configured | 2276 | 42277 | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 | 42278 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 | 42279 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 | 42280 | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 | 42281 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 | 42282 | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 | 42283 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 | 42284 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 | 42285 | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 | 42286 | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 | 42287 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 | 42288 | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 | 42289 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 | 42290 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 | 42291 | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 | 42292 | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | 42293 | [11 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 | 42294 | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | 42295 | [11 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 | 42296 | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 | 42297 | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - | METROLOGY POINTS | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 | 42301 | Displacement PF Avg Element | dPF | Metrology | float32 | R | 92300 | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | 42302 | [11 empty] | ALL
Displacement PF CH1 (MSW) | 2302 | 42303 | Displacement PF CH1 (A) | dPF | Metrology | float32 | R | 92302 | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | 42304 | [11 empty] | ALL
Displacement PF CH2 (MSW) | 2304 | 42305 | Displacement PF CH2 (B) | dPF | Metrology | float32 | R | 92304 | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | 42306 | [11 empty] | ALL
Displacement PF CH3 (MSW) | 2306 | 42307 | Displacement PF CH3 (C) | dPF | Metrology | float32 | R | 92306 | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | 42308 | [11 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 | 42309 | Avg Apparent PF Element | aPF | Metrology | float32 | R | 92308 | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | 42310 | [11 empty] | ALL
Apparent PF CH1 (MSW) | 2310 | 42311 | Apparent PF CH1 (A) | aPF | Metrology | float32 | R | 92310 | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | 42312 | [11 empty] | ALL
Apparent PF CH2 (MSW) | 2312 | 42313 | Apparent PF CH2 (B) | aPF | Metrology | float32 | R | 92312 | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | 42314 | [11 empty] | ALL
Apparent PF CH3 (MSW) | 2314 | 42315 | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R | 92314 | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | 42316 | [11 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 | 42317 | Distortion PF Avg Element | tPF | Metrology | float32 | R | 92316 | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | 42318 | [11 empty] | ALL
Distortion PF CH1 (MSW) | 2318 | 42319 | Distortion PF CH1 (A) | tPF | Metrology | float32 | R | 92318 | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | 42320 | [11 empty] | ALL
Distortion PF CH2 (MSW) | 2320 | 42321 | Distortion PF CH2 (B) | tPF | Metrology | float32 | R | 92320 | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | 42322 | [11 empty] | ALL
Distortion PF CH3 (MSW) | 2322 | 42323 | Distortion PF CH3 (C) | tPF | Metrology | float32 | R | 92322 | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | 42324 | [11 empty] | ALL
THD Avg Element (MSW) | 2324 | 42325 | THD Avg Element | % | Metrology | float32 | R | 92324 | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | 42326 | [11 empty] | ALL
THD CH1 (MSW) | 2326 | 42327 | THD CH1 (A) | % | Metrology | float32 | R | 92326 | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | 42328 | [11 empty] | ALL
THD CH2 (MSW) | 2328 | 42329 | THD CH2 (B) | % | Metrology | float32 | R | 92328 | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | 42330 | [11 empty] | ALL
THD CH3 (MSW) | 2330 | 42331 | THD CH3 (C) | % | Metrology | float32 | R | 92330 | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | 42332 | [11 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 | 42333 | Power Demand Max Interval Element | kW | Metrology | float32 | R | 92332 | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | 42334 | [11 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 | 42335 | Power Demand This Interval Element | kW | Metrology | float32 | R | 92334 | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | 42336 | [11 empty] | ALL
VA Peak Demand Element (MSW) | 2336 | 42337 | VA Demand Max Interval Element | kVA | Metrology | float32 | R | 92336 | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | 42338 | [11 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 | 42339 | VA Demand This Interval Element | kVA | Metrology | float32 | R | 92338 | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | 42340 | [11 empty] | ALL
Not Used | 2340 | 42341 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 | 42342 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 | 42343 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 | 42344 | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 | 42345 | Energy Net Sum Element | kWh | Metrology | float32 | R | 92344 | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | 42346 | [8 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 | 42347 | Energy Net CH1 | kWh | Metrology | float32 | R | 92346 | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | 42348 | [8 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 | 42349 | Energy Net CH2 | kWh | Metrology | float32 | R | 92348 | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | 42350 | [8 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 | 42351 | Energy Net CH3 | kWh | Metrology | float32 | R | 92350 | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | 42352 | [8 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 | 42353 | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R | 92352 | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | 42354 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 | 42355 | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R | 92354 | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | 42356 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 | 42357 | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R | 92356 | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | 42358 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 | 42359 | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R | 92358 | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | 42360 | [8 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 | 42361 | VARh Net Sum Element | kVArh | Metrology | float32 | R | 92360 | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | 42362 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 | 42363 | VARh Net CH1 | kVArh | Metrology | float32 | R | 92362 | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | 42364 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 | 42365 | VARh Net CH2 | kVArh | Metrology | float32 | R | 92364 | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | 42366 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 | 42367 | VARh Net CH3 | kVArh | Metrology | float32 | R | 92366 | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | 42368 | [8 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 | 42369 | Time Since Reset MSW | Sec | Metrology | uint32 |  | 2368 | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 | 42370 | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 | 42371 | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 | 42372 | CH1 Angle | Deg | Metrology | float32 | R | 92371 | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | 42373 | [8 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 | 42374 | CH2 Angle | Deg | Metrology | float32 | R | 92373 | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | 42375 | [8 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 | 42376 | CH3 Angle | Deg | Metrology | float32 | R | 92375 | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | 42377 | [11 empty] | ALL
Phase Chek System Status | 2377 | 42378 | System Phase Check Status |  | Metrology | bitfield16 | R | 2377 | BV | Phase Check System Status | system | 0,1 | 0 (All Channels OK), 1(Somewhere a channel is reading a dPF < 0.55), check register 2378 for each Element | ALL
Phase Chek Element Status | 2378 | 42379 | Element Phase Check Status |  | Metrology | bitfield16 | R | 92378 | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 | 42380 | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 | 42381 | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 | 42382 | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 | 42392 | Element Angle |  | Metrology | float | R | 92391 | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | 42393 | [11 empty] | ALL
PULSE INPUTS | - | - | PULSE INPUTS | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 | 42401 | Pulse Input 1 Enable |  | Config | uint16 | R/W | 2400 | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 | 42402 | Pulse Input 1 Scale Factor |  | Config | float32 | R/W | 2401 | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 | 42403 |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 | 42404 | Pulse Input 1 Units |  | Config | string(4) | R/W | 2403 | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 | 42405 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 | 42406 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 | 42407 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 | 42408 | Pulse Input 1 Accumulator |  | Metrology | float32 | R | 2407 | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | 42409 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 | 42410 | Pulse Input 1 Accumulator Clear |  | User | unit16 | W | 2409 | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 | 42411 | Pulse Input 2 Enable |  | Config | uint16 | R/W | 2410 | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 | 42412 | Pulse Input 2 Scale Factor |  | Config | float32 | R/W | 2411 | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | 42413 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 | 42414 | Pulse Input 2 Units |  | Config | string(4) | R/W | 2413 | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 | 42415 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 | 42416 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 | 42417 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 | 42418 | Pulse Input 2 Accumulator |  | Metrology | float32 | R | 2417 | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | 42419 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 | 42420 | Pulse Input 2 Accumulator Clear |  | User | unit16 | W | 2419 | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 | 42421 | Pulse Input 3 Enable |  | Config | uint16 | R/W | 2420 | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 | 42422 | Pulse Input 3 Scale Factor |  | Config | float32 | R/W | 2421 | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | 42423 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 | 42424 | Pulse Input 3 Units |  | Config | string(4) | R/W | 2423 | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 | 42425 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 | 42426 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 | 42427 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 | 42428 | Pulse Input 3 Accumulator |  | Metrology | float32 | R | 2427 | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | 42429 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 | 42430 | Pulse Input 3 Accumulator Clear |  | User |  | W | 2429 | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 | 42431 | Pulse Input 4 Enable |  | Config | uint16 | R/W | 2430 | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 | 42432 | Pulse Input 4 Scale Factor |  | Config | float32 | R/W | 2431 | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | 42433 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 | 42434 | Pulse Input 4 Units |  | Config | string(4) | R/W | 2433 | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 | 42435 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 | 42436 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 | 42437 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 | 42438 | Pulse Input 4 Accumulator |  | Metrology | float32 | R | 2437 | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | 42439 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 | 42440 | Pulse Input 4 Accumulator Clear |  | User | unit16 | W | 2439 | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - | ALARMS | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 | 42452 | State of Alarm |  | Metrology | uint16 | R/W | 2451 | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 | 42453 | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 | 42454 | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 | 42455 | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 | 42456 | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 | 42457 | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 | 42458 | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 | 42459 | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W | 2458 | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 | 42460 | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W | 2459 | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Range Vin1 L1N Under | 2460 | 42461 | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W | 2460 | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 | 42462 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2N Under | 2462 | 42463 | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W | 2462 | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 | 42464 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3N Under | 2464 | 42465 | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W | 2464 | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 | 42466 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L1L2 Under | 2466 | 42467 | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W | 2466 | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 | 42468 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2L3 Under | 2468 | 42469 | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W | 2468 | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 | 42470 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3L1 Under | 2470 | 42471 | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W | 2470 | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 | 42472 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin2 L1N Under | 2472 | 42473 | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W | 2472 | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 | 42474 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2N Under | 2474 | 42475 | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W | 2474 | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 | 42476 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3N Under | 2476 | 42477 | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W | 2476 | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 | 42478 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L1L2 Under | 2478 | 42479 | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W | 2478 | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 | 42480 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2L3 Under | 2480 | 42481 | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W | 2480 | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 | 42482 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3L1 Under | 2482 | 42483 | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W | 2482 | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 | 42484 | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 | 42485 | Voltage Alarm Persistence | Sec | Config | uint16 | R/W | 2484 | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 | 42486 | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R | 2485 | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 | 42487 | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 | 42488 | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R | 2487 | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 | 42489 | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 | 42490 | Real Time Clock MSW |  | Config | uint16 | R/W | 2489 | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 | 42491 | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - | USER CONFIG POINTS 2 | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 | 42602 | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 | 42603 | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 | 42604 | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 | 42605 | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 | 42606 | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 | 42607 | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 | 42608 | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 | 42609 | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 | 42610 | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 | 42611 | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 | 42612 | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 | 42613 | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 | 42614 | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 | 42615 | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 | 42616 | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 | 42617 | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 | 42618 | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 | 42619 | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 | 42620 | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 | 42621 | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 | 42622 | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 | 42623 | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 | 42624 | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 | 42625 | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 | 42626 | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 | 42627 | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 | 42628 | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 | 42629 | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 | 42630 | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 | 42631 | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 | 42632 | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 | 42633 | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 | 42634 | BACnet Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | 2634 | 42635 | BACnet Description 1 | [8 empty] | 2 Char |  | ALL
BACnet Description 2 | 2635 | 42636 | BACnet Description 2 | [8 empty] | 2 Char |  | ALL
BACnet Description 3 | 2636 | 42637 | BACnet Description 3 | [8 empty] | 2 Char |  | ALL
BACnet Description 4 | 2637 | 42638 | BACnet Description 4 | [8 empty] | 2 Char |  | ALL
BACnet Description 5 | 2638 | 42639 | BACnet Description 5 | [8 empty] | 2 Char |  | ALL
BACnet Description 6 | 2639 | 42640 | BACnet Description 6 | [8 empty] | 2 Char |  | ALL
BACnet Description 7 | 2640 | 42641 | BACnet Description 7 | [8 empty] | 2 Char |  | ALL
BACnet Description 8 | 2641 | 42642 | BACnet Description 8 | [8 empty] | 2 Char |  | ALL
BACnet Description 9 | 2642 | 42643 | BACnet Description 9 | [8 empty] | 2 Char |  | ALL
BACnet Description 10 | 2643 | 42644 | BACnet Description 10 | [8 empty] | 2 Char |  | ALL
BACnet Description 11 | 2644 | 42645 | BACnet Description 11 | [8 empty] | 2 Char |  | ALL
BACnet Description 12 | 2645 | 42646 | BACnet Description 12 | [8 empty] | 2 Char |  | ALL
BACnet Description 13 | 2646 | 42647 | BACnet Description 13 | [8 empty] | 2 Char |  | ALL
BACnet Description 14 | 2647 | 42648 | BACnet Description 14 | [8 empty] | 2 Char |  | ALL
BACnet Description 15 | 2648 | 42649 | BACnet Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
VERIS EMULATION LEGACY REGISTERS | - | - | VERIS EMULATION LEGACY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Veris Emulation Mode | 2200 | 42201 | Set to Veris Emulation Mode |  | Config | uint16 | R/W |  |  |  | system | 0-1 | 1 = Report Slave ID as Veris Model H8036 | ALL
kWh System LSW | 0 | 40001 | kWh System LSW | kWh | Veris | uint32 | R |  |  |  | element |  |  | ALL
kWh System MSW | 1 | 40002 | kWh System MSW | kWh | Veris |  | R |  |  |  | element |  |  | ALL
kW System | 2 | 40003 | kW System | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVAR System | 3 | 40004 | kVAR System | kVAR | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVA System | 4 | 40005 | kVA System | kVA | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF System | 5 | 40006 | Apparent PF System | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts Line to Line Avg | 6 | 40007 | Volts Line to Line Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts Line to Neutral Avg | 7 | 40008 | Volts Line to Neutral Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps System Avg | 8 | 40009 | Amps System Avg | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L1 | 9 | 40010 | kW L1 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L2 | 10 | 40011 | kW L2 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L3 | 11 | 40012 | kW L3 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L1 | 12 | 40013 | Apparent PF L1 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L2 | 13 | 40014 | Apparent PF L2 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L3 | 14 | 40015 | Apparent PF L3 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts L1 to L2 | 15 | 40016 | Volts L1 to L2 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to L3 | 16 | 40017 | Volts L2 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to L3 | 17 | 40018 | Volts L1 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to Neutral | 18 | 40019 | Volts L1 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to Neutral | 19 | 40020 | Volts L2 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L3 to Neutral | 20 | 40021 | Volts L3 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps L1 | 21 | 40022 | Amps L1 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L2 | 22 | 40023 | Amps L2 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L3 | 23 | 40024 | Amps L3 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW System Avg | 24 | 40025 | kW System Avg | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Now | 25 | 40026 | kW Demand Sys Now (was Min) | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Max | 26 | 40027 | kW Demand Sys Max | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL

## K
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS --> | 11
BACNET OBJECT FLOOR --> | 100000
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 | 41002 | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | 41003 | [8 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 | 41004 | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 | 41005 | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 | 41006 | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | 41007 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | 41008 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | 41009 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | 41010 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | 41011 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | 41012 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | 41013 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | 41014 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | 41015 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | 41016 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | 41017 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | 41018 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | 41019 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | 41020 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | 41021 | [8 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 | 41022 | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | 41023 | [8 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | 41024 | [8 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | 41025 | [8 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | 41026 | [8 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | 41027 | [8 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | 41028 | [8 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | 41029 | [8 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | 41030 | [8 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | 41031 | [8 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | 41032 | [8 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | 41033 | [8 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | 41034 | [8 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | 41035 | [8 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | 41036 | [8 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | 41037 | [8 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 | 41038 | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | 41039 | [8 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | 41040 | [8 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | 41041 | [8 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | 41042 | [8 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | 41043 | [8 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | 41044 | [8 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | 41045 | [8 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 | 41046 | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | 41047 | [8 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | 41048 | [8 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | 41049 | [8 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | 41050 | [8 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | 41051 | [8 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | 41052 | [8 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | 41053 | [8 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 | 41054 | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | 41055 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | 41056 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | 41057 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | 41058 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | 41059 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | 41060 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | 41061 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | 41062 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | 41063 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | 41064 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | 41065 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | 41066 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | 41067 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | 41068 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | 41069 | [8 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 | 41070 | Modbus Device Address |  |  | unit16 | R/W | 1069 | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | 41071 | [8 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 | 41072 | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 | 41073 | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 | 41074 | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | 41075 | [8 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | 41076 | [8 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | 41077 | [8 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 | 41078 | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 | 41079 | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 | 41080 | IP Address |  |  | string(8) | R/W | 1079 | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | 41081 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | 41082 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | 41083 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | 41084 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | 41085 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | 41086 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | 41087 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 | 41088 | Netmask |  |  | string(8) | R/W | 1087 | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | 41089 | [8 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | 41090 | [8 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | 41091 | [8 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | 41092 | [8 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | 41093 | [8 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | 41094 | [8 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | 41095 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 | 41096 | Gateway |  |  | string(8) | R/W | 1095 | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | 41097 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | 41098 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | 41099 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | 41100 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | 41101 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | 41102 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | 41103 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 | 41104 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | 41105 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | 41106 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | 41107 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | 41108 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | 41109 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | 41110 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | 41111 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 | 41112 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | 41113 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | 41114 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | 41115 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | 41116 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | 41117 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | 41118 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | 41119 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 | 41120 | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | 41121 | [8 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | 41122 | [8 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | 41123 | [8 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 | 41124 | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | 41125 | [9 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 | 41126 | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 | 41127 | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 | 41128 | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | 41129 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | 41130 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | 41131 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 | 41132 | Interface baud rate in bits per second |  |  | uint32 | R/W | 1131 | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | 41133 | [8 empty] | system |  |  | ALL
SERIAL BITS | 1133 | 41134 | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 | 41135 | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 | 41136 | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 | 41137 | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 | 41138 | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 | 41139 | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 | 41140 | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 | 41141 | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 | 41142 | Current Avg Element | A | Metrology | float32 | R | 101141 | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | 41143 | [8 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 | 41144 | Current CH1 (A) | A | Metrology | float32 | R | 101143 | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | 41145 | [8 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 | 41146 | Current CH2 (B) | A | Metrology | float32 | R | 101145 | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | 41147 | [8 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 | 41148 | Current CH3 (C) | A | Metrology | float32 | R | 101147 | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | 41149 | [8 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 | 41150 | Voltage L to N Avg Element | V | Metrology | float32 | R | 101149 | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | 41151 | [8 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 | 41152 | Voltage L1 to N (AN) | V | Metrology | float32 | R | 101151 | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | 41153 | [8 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 | 41154 | Voltage L2 to N (BN) | V | Metrology | float32 | R | 101153 | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | 41155 | [8 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 | 41156 | Voltage L3 to N (CN) | V | Metrology | float32 | R | 101155 | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | 41157 | [8 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 | 41158 | Voltage L to L Avg Element | V | Metrology | float32 | R | 101157 | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | 41159 | [8 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 | 41160 | Voltage L1 to L2 (AB) | V | Metrology | float32 | R | 101159 | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | 41161 | [8 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 | 41162 | Voltage L2 to L3 (BC) | V | Metrology | float32 | R | 101161 | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | 41163 | [8 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 | 41164 | Voltage L3 to L1 (CA) | V | Metrology | float32 | R | 101163 | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | 41165 | [8 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 | 41166 | Line Frequency | Hz | Metrology | float32 | R | 101165 | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | 41167 | [8 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 | 41168 | Power Sum Element | kW | Metrology | float32 | R | 101167 | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | 41169 | [8 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 | 41170 | Power CH1 (A) | kW | Metrology | float32 | R | 101169 | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | 41171 | [8 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 | 41172 | Power CH2 (B) | kW | Metrology | float32 | R | 101171 | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | 41173 | [8 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 | 41174 | Power CH3 (C) | kW | Metrology | float32 | R | 101173 | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | 41175 | [8 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 | 41176 | VA Sum Element | kVA | Metrology | float32 | R | 101175 | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | 41177 | [8 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 | 41178 | VA CH1 (A) | kVA | Metrology | float32 | R | 101177 | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | 41179 | [8 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 | 41180 | VA CH2 (B) | kVA | Metrology | float32 | R | 101179 | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | 41181 | [8 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 | 41182 | VA CH3 (C) | kVA | Metrology | float32 | R | 101181 | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | 41183 | [8 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 | 41184 | VAR Sum Element | kVAr | Metrology | float32 | R | 101183 | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | 41185 | [8 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 | 41186 | VAR CH1 (A) | kVAr | Metrology | float32 | R | 101185 | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | 41187 | [8 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 | 41188 | VAR CH2 (B) | kVAr | Metrology | float32 | R | 101187 | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | 41189 | [8 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 | 41190 | VAR CH3 (C) | kVAr | Metrology | float32 | R | 101189 | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | 41191 | [8 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 | 41192 | Apparent PF Avg Element | PF | Metrology | float32 | R | 101191 | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | 41193 | [8 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 | 41194 | Apparent PF CH1 (A) | PF | Metrology | float32 | R | 101193 | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | 41195 | [8 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 | 41196 | Apparent PF CH2 (B) | PF | Metrology | float32 | R | 101195 | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | 41197 | [8 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 | 41198 | Apparent PF CH3 ( C) | PF | Metrology | float32 | R | 101197 | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | 41199 | [8 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 | 41200 | Exported Energy Sum Element | kWh | Metrology | float32 | R | 101199 | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | 41201 | [8 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 | 41202 | Exported Energy CH1 (A) | kWh | Metrology | float32 | R | 101201 | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | 41203 | [8 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 | 41204 | Exported Energy CH2 (B) | kWh | Metrology | float32 | R | 101203 | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | 41205 | [8 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 | 41206 | Exported Energy CH3 (C) | kWh | Metrology | float32 | R | 101205 | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | 41207 | [8 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 | 41208 | Imported Energy Sum Element | kWh | Metrology | float32 | R | 101207 | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | 41209 | [8 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 | 41210 | Imported Energy CH1 (A) | kWh | Metrology | float32 | R | 101209 | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | 41211 | [8 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 | 41212 | Imported Energy CH2 (B) | kWh | Metrology | float32 | R | 101211 | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | 41213 | [8 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 | 41214 | Imported Energy CH3 (C) | kWh | Metrology | float32 | R | 101213 | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | 41215 | [8 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 | 41216 | Exported VAh Sum Element | kVAh | Metrology | float32 | R | 101215 | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | 41217 | [8 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 | 41218 | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R | 101217 | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | 41219 | [8 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 | 41220 | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R | 101219 | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | 41221 | [8 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 | 41222 | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R | 101221 | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | 41223 | [8 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 | 41224 | Imported VAh Sum Element | kVAh | Metrology | float32 | R | 101223 | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | 41225 | [8 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 | 41226 | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R | 101225 | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | 41227 | [8 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 | 41228 | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R | 101227 | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | 41229 | [8 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 | 41230 | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R | 101229 | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | 41231 | [8 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 | 41232 | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R | 101231 | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | 41233 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 | 41234 | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R | 101233 | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | 41235 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 | 41236 | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R | 101235 | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | 41237 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 | 41238 | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R | 101237 | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | 41239 | [8 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 | 41240 | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R | 101239 | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | 41241 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 | 41242 | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R | 101241 | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | 41243 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 | 41244 | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R | 101243 | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | 41245 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 | 41246 | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R | 101245 | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | 41247 | [8 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 | 41248 | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R | 101247 | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | 41249 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 | 41250 | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R | 101249 | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | 41251 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 | 41252 | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R | 101251 | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | 41253 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 | 41254 | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R | 101253 | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | 41255 | [8 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 | 41256 | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R | 101255 | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | 41257 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 | 41258 | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R | 101257 | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | 41259 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 | 41260 | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R | 101259 | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | 41261 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 | 41262 | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R | 101261 | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | 41263 | [8 empty] | element |  |  | ALL
Events MSW | 1263 | 41264 | Events MSW |  |  | bitfield32 | R | 1263 | AI | Events | system |  |  | ALL
Events LSW | 1264 | 41265 | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 | 41266 | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 | 41267 | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
FACTORY REGISTERS | - | - | FACTORY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Factory Unlock Register | 2000 | 42001 | Factory Unlock Register |  | Factory | unit16 | R/W |  |  |  | system |  | Reserved | ALL
Factory Reset | 2001 | 42002 | Factory Reset |  | Factory | unit16 | R/W |  |  |  | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
OEM Vendor ID | 2002 | 42003 | OEM Vendor ID |  | Factory | unit16 | R |  |  |  | system |  | Reserved | ALL
FACTORY_CONFIG | 2003 | 42004 | Factory Config |  | Factory | unit16 | R |  |  |  | system | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable | ALL
USER COMMAND POINTS | - | - | USER COMMAND POINTS | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 | 42101 | Reset (software) processor |  | User | unit16 | W | 2100 | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 | 42102 | Clear all accumulated measurements (CAM) |  | User | unit16 | W | 2101 | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 | 42103 | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W | 102102 | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 | 42104 | Clear Peak Demand Element |  | User | unit16 | W | 102103 | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 | 42105 | Clear Peak Demand All |  | User | unit16 | W | 2104 | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 | 42106 | Reset to User Defaults |  | User | unit16 | W | 2105 | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - | USER CONFIG POINTS | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 | 42202 | Sliding or Fixed |  | Config | enum16 | R | 2201 | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 | 42203 | Demand Window | Min | Config | uint16 | R | 2202 | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 | 42204 | Volt Multiplier VINPUT1 |  | Config | float32 | R/W | 2203 | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | 42205 | [8 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 | 42206 | Volt Multiplier VINPUT2 |  | Config | float32 | R/W | 2205 | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | 42207 | [8 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 | 42208 | Service Type |  | Config | enum16 | R/W | 102207 | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 | 42209 | Snap MV Threshold | PER | Config | float32 | R/W | 2208 | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | 42210 | [8 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 | 42211 | Snap Rog Threshold | PER | Config | float32 | R/W | 2210 | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | 42212 | [8 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 | 42213 | Snap Volt Threshold | V | Config | float32 | R/W | 2212 | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | 42214 | [8 empty] | system |  |  | ALL
Communications Mode | 2214 | 42215 | Communications Mode |  | Config |  |  | 2214 | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 | 42216 | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W | 2215 | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | 42217 | [8 empty] | system |  |  | ALL
Voltage Input Element | 2217 | 42218 | Element Voltage Input |  | Config | enum16 | R/W | 102217 | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 | 42219 | CT1 RANGE | A | Config | float32 | R/W | 102218 | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | 42220 | [8 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 | 42221 | Voltage Reference for CT1 |  | Config | enum16 | R/W | 102220 | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 | 42222 | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W | 102221 | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | 42223 | [8 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 | 42224 | CT1 TYPE |  | Config | enum16 | R/W | 102223 | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 | 42225 | CT1 PHASE SHIFT | Deg | Config | float32 | R/W | 102224 | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | 42226 | [8 empty] | element |  |  | ALL
CH1 CT Sign | 2226 | 42227 | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W | 102226 | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 | 42228 | CT2 RANGE | A | Config | float32 | R/W | 102227 | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | 42229 | [8 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 | 42230 | Voltage Reference for CT2 |  | Config | enum16 | R/W | 102229 | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 | 42231 | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W | 102230 | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | 42232 | [8 empty] | element | >0 |  | ALL
CH2 CT type | 2232 | 42233 | CT2 TYPE |  | Config | enum16 | R/W | 102232 | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 | 42234 | CT2 PHASE SHIFT | Deg | Config | float32 | R/W | 102233 | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | 42235 | [8 empty] | element |  |  | ALL
CH2 CT Sign | 2235 | 42236 | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W | 102235 | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 | 42237 | CT3 INTEGER | A | Config | float32 | R/W | 102236 | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | 42238 | [8 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 | 42239 | Voltage Reference for CT3 |  | Config | enum16 | R/W | 102238 | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 | 42240 | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W | 102239 | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | 42241 | [8 empty] | element | >0 |  | ALL
CH3 CT type | 2241 | 42242 | CT3 TYPE |  | Config | enum16 | R/W | 102241 | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 | 42243 | CT3 PHASE SHIFT | Deg | Config | float32 | R/W | 102242 | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | 42244 | [8 empty] | element |  |  | ALL
CH3 CT Sign | 2244 | 42245 | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W | 102244 | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 | 42246 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 | 42247 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 | 42248 | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 | 42249 | PF Sign Convention |  | Config | uint16 | R/W | 2248 | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 | 42250 | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 | 42251 | BACnet UDP Port |  | Config | uint16 | R/W | 2250 | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 | 42252 | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 | 42253 | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | 42254 | [8 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 | 42261 | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | 42262 | [11 empty] | ALL
BACnet Max Info Frames | 2262 | 42263 | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 | 42264 | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 | 42265 | BBMD IP Address |  | Config | string(16) | R/W | 2264 | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | 42266 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | 42267 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | 42268 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | 42269 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | 42270 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | 42271 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | 42272 | [9 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 | 42273 | LCD/WebApp Read Password |  | Config | uint16 | R/W | 2272 | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 | 42274 | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 | 42275 | Customer Line frequency |  | Config | float | R/W | 2274 | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | 42276 | [10 empty] | Reserved | ALL
Communications Interface Configured | 2276 | 42277 | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 | 42278 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 | 42279 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 | 42280 | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 | 42281 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 | 42282 | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 | 42283 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 | 42284 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 | 42285 | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 | 42286 | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 | 42287 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 | 42288 | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 | 42289 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 | 42290 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 | 42291 | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 | 42292 | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | 42293 | [11 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 | 42294 | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | 42295 | [11 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 | 42296 | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 | 42297 | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - | METROLOGY POINTS | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 | 42301 | Displacement PF Avg Element | dPF | Metrology | float32 | R | 102300 | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | 42302 | [11 empty] | ALL
Displacement PF CH1 (MSW) | 2302 | 42303 | Displacement PF CH1 (A) | dPF | Metrology | float32 | R | 102302 | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | 42304 | [11 empty] | ALL
Displacement PF CH2 (MSW) | 2304 | 42305 | Displacement PF CH2 (B) | dPF | Metrology | float32 | R | 102304 | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | 42306 | [11 empty] | ALL
Displacement PF CH3 (MSW) | 2306 | 42307 | Displacement PF CH3 (C) | dPF | Metrology | float32 | R | 102306 | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | 42308 | [11 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 | 42309 | Avg Apparent PF Element | aPF | Metrology | float32 | R | 102308 | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | 42310 | [11 empty] | ALL
Apparent PF CH1 (MSW) | 2310 | 42311 | Apparent PF CH1 (A) | aPF | Metrology | float32 | R | 102310 | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | 42312 | [11 empty] | ALL
Apparent PF CH2 (MSW) | 2312 | 42313 | Apparent PF CH2 (B) | aPF | Metrology | float32 | R | 102312 | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | 42314 | [11 empty] | ALL
Apparent PF CH3 (MSW) | 2314 | 42315 | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R | 102314 | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | 42316 | [11 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 | 42317 | Distortion PF Avg Element | tPF | Metrology | float32 | R | 102316 | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | 42318 | [11 empty] | ALL
Distortion PF CH1 (MSW) | 2318 | 42319 | Distortion PF CH1 (A) | tPF | Metrology | float32 | R | 102318 | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | 42320 | [11 empty] | ALL
Distortion PF CH2 (MSW) | 2320 | 42321 | Distortion PF CH2 (B) | tPF | Metrology | float32 | R | 102320 | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | 42322 | [11 empty] | ALL
Distortion PF CH3 (MSW) | 2322 | 42323 | Distortion PF CH3 (C) | tPF | Metrology | float32 | R | 102322 | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | 42324 | [11 empty] | ALL
THD Avg Element (MSW) | 2324 | 42325 | THD Avg Element | % | Metrology | float32 | R | 102324 | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | 42326 | [11 empty] | ALL
THD CH1 (MSW) | 2326 | 42327 | THD CH1 (A) | % | Metrology | float32 | R | 102326 | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | 42328 | [11 empty] | ALL
THD CH2 (MSW) | 2328 | 42329 | THD CH2 (B) | % | Metrology | float32 | R | 102328 | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | 42330 | [11 empty] | ALL
THD CH3 (MSW) | 2330 | 42331 | THD CH3 (C) | % | Metrology | float32 | R | 102330 | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | 42332 | [11 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 | 42333 | Power Demand Max Interval Element | kW | Metrology | float32 | R | 102332 | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | 42334 | [11 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 | 42335 | Power Demand This Interval Element | kW | Metrology | float32 | R | 102334 | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | 42336 | [11 empty] | ALL
VA Peak Demand Element (MSW) | 2336 | 42337 | VA Demand Max Interval Element | kVA | Metrology | float32 | R | 102336 | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | 42338 | [11 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 | 42339 | VA Demand This Interval Element | kVA | Metrology | float32 | R | 102338 | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | 42340 | [11 empty] | ALL
Not Used | 2340 | 42341 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 | 42342 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 | 42343 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 | 42344 | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 | 42345 | Energy Net Sum Element | kWh | Metrology | float32 | R | 102344 | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | 42346 | [8 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 | 42347 | Energy Net CH1 | kWh | Metrology | float32 | R | 102346 | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | 42348 | [8 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 | 42349 | Energy Net CH2 | kWh | Metrology | float32 | R | 102348 | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | 42350 | [8 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 | 42351 | Energy Net CH3 | kWh | Metrology | float32 | R | 102350 | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | 42352 | [8 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 | 42353 | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R | 102352 | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | 42354 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 | 42355 | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R | 102354 | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | 42356 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 | 42357 | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R | 102356 | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | 42358 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 | 42359 | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R | 102358 | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | 42360 | [8 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 | 42361 | VARh Net Sum Element | kVArh | Metrology | float32 | R | 102360 | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | 42362 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 | 42363 | VARh Net CH1 | kVArh | Metrology | float32 | R | 102362 | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | 42364 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 | 42365 | VARh Net CH2 | kVArh | Metrology | float32 | R | 102364 | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | 42366 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 | 42367 | VARh Net CH3 | kVArh | Metrology | float32 | R | 102366 | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | 42368 | [8 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 | 42369 | Time Since Reset MSW | Sec | Metrology | uint32 |  | 2368 | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 | 42370 | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 | 42371 | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 | 42372 | CH1 Angle | Deg | Metrology | float32 | R | 102371 | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | 42373 | [8 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 | 42374 | CH2 Angle | Deg | Metrology | float32 | R | 102373 | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | 42375 | [8 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 | 42376 | CH3 Angle | Deg | Metrology | float32 | R | 102375 | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | 42377 | [11 empty] | ALL
Phase Chek System Status | 2377 | 42378 | System Phase Check Status |  | Metrology | bitfield16 | R | 2377 | BV | Phase Check System Status | system | 0,1 | 0 (All Channels OK), 1(Somewhere a channel is reading a dPF < 0.55), check register 2378 for each Element | ALL
Phase Chek Element Status | 2378 | 42379 | Element Phase Check Status |  | Metrology | bitfield16 | R | 102378 | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 | 42380 | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 | 42381 | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 | 42382 | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 | 42392 | Element Angle |  | Metrology | float | R | 102391 | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | 42393 | [11 empty] | ALL
PULSE INPUTS | - | - | PULSE INPUTS | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 | 42401 | Pulse Input 1 Enable |  | Config | uint16 | R/W | 2400 | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 | 42402 | Pulse Input 1 Scale Factor |  | Config | float32 | R/W | 2401 | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 | 42403 |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 | 42404 | Pulse Input 1 Units |  | Config | string(4) | R/W | 2403 | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 | 42405 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 | 42406 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 | 42407 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 | 42408 | Pulse Input 1 Accumulator |  | Metrology | float32 | R | 2407 | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | 42409 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 | 42410 | Pulse Input 1 Accumulator Clear |  | User | unit16 | W | 2409 | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 | 42411 | Pulse Input 2 Enable |  | Config | uint16 | R/W | 2410 | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 | 42412 | Pulse Input 2 Scale Factor |  | Config | float32 | R/W | 2411 | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | 42413 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 | 42414 | Pulse Input 2 Units |  | Config | string(4) | R/W | 2413 | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 | 42415 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 | 42416 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 | 42417 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 | 42418 | Pulse Input 2 Accumulator |  | Metrology | float32 | R | 2417 | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | 42419 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 | 42420 | Pulse Input 2 Accumulator Clear |  | User | unit16 | W | 2419 | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 | 42421 | Pulse Input 3 Enable |  | Config | uint16 | R/W | 2420 | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 | 42422 | Pulse Input 3 Scale Factor |  | Config | float32 | R/W | 2421 | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | 42423 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 | 42424 | Pulse Input 3 Units |  | Config | string(4) | R/W | 2423 | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 | 42425 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 | 42426 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 | 42427 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 | 42428 | Pulse Input 3 Accumulator |  | Metrology | float32 | R | 2427 | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | 42429 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 | 42430 | Pulse Input 3 Accumulator Clear |  | User |  | W | 2429 | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 | 42431 | Pulse Input 4 Enable |  | Config | uint16 | R/W | 2430 | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 | 42432 | Pulse Input 4 Scale Factor |  | Config | float32 | R/W | 2431 | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | 42433 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 | 42434 | Pulse Input 4 Units |  | Config | string(4) | R/W | 2433 | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 | 42435 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 | 42436 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 | 42437 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 | 42438 | Pulse Input 4 Accumulator |  | Metrology | float32 | R | 2437 | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | 42439 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 | 42440 | Pulse Input 4 Accumulator Clear |  | User | unit16 | W | 2439 | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - | ALARMS | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 | 42452 | State of Alarm |  | Metrology | uint16 | R/W | 2451 | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 | 42453 | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 | 42454 | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 | 42455 | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 | 42456 | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 | 42457 | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 | 42458 | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 | 42459 | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W | 2458 | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 | 42460 | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W | 2459 | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Range Vin1 L1N Under | 2460 | 42461 | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W | 2460 | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 | 42462 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2N Under | 2462 | 42463 | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W | 2462 | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 | 42464 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3N Under | 2464 | 42465 | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W | 2464 | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 | 42466 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L1L2 Under | 2466 | 42467 | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W | 2466 | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 | 42468 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2L3 Under | 2468 | 42469 | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W | 2468 | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 | 42470 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3L1 Under | 2470 | 42471 | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W | 2470 | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 | 42472 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin2 L1N Under | 2472 | 42473 | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W | 2472 | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 | 42474 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2N Under | 2474 | 42475 | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W | 2474 | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 | 42476 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3N Under | 2476 | 42477 | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W | 2476 | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 | 42478 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L1L2 Under | 2478 | 42479 | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W | 2478 | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 | 42480 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2L3 Under | 2480 | 42481 | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W | 2480 | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 | 42482 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3L1 Under | 2482 | 42483 | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W | 2482 | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 | 42484 | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 | 42485 | Voltage Alarm Persistence | Sec | Config | uint16 | R/W | 2484 | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 | 42486 | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R | 2485 | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 | 42487 | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 | 42488 | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R | 2487 | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 | 42489 | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 | 42490 | Real Time Clock MSW |  | Config | uint16 | R/W | 2489 | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 | 42491 | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - | USER CONFIG POINTS 2 | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 | 42602 | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 | 42603 | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 | 42604 | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 | 42605 | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 | 42606 | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 | 42607 | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 | 42608 | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 | 42609 | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 | 42610 | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 | 42611 | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 | 42612 | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 | 42613 | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 | 42614 | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 | 42615 | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 | 42616 | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 | 42617 | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 | 42618 | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 | 42619 | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 | 42620 | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 | 42621 | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 | 42622 | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 | 42623 | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 | 42624 | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 | 42625 | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 | 42626 | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 | 42627 | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 | 42628 | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 | 42629 | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 | 42630 | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 | 42631 | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 | 42632 | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 | 42633 | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 | 42634 | BACnet Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | 2634 | 42635 | BACnet Description 1 | [8 empty] | 2 Char |  | ALL
BACnet Description 2 | 2635 | 42636 | BACnet Description 2 | [8 empty] | 2 Char |  | ALL
BACnet Description 3 | 2636 | 42637 | BACnet Description 3 | [8 empty] | 2 Char |  | ALL
BACnet Description 4 | 2637 | 42638 | BACnet Description 4 | [8 empty] | 2 Char |  | ALL
BACnet Description 5 | 2638 | 42639 | BACnet Description 5 | [8 empty] | 2 Char |  | ALL
BACnet Description 6 | 2639 | 42640 | BACnet Description 6 | [8 empty] | 2 Char |  | ALL
BACnet Description 7 | 2640 | 42641 | BACnet Description 7 | [8 empty] | 2 Char |  | ALL
BACnet Description 8 | 2641 | 42642 | BACnet Description 8 | [8 empty] | 2 Char |  | ALL
BACnet Description 9 | 2642 | 42643 | BACnet Description 9 | [8 empty] | 2 Char |  | ALL
BACnet Description 10 | 2643 | 42644 | BACnet Description 10 | [8 empty] | 2 Char |  | ALL
BACnet Description 11 | 2644 | 42645 | BACnet Description 11 | [8 empty] | 2 Char |  | ALL
BACnet Description 12 | 2645 | 42646 | BACnet Description 12 | [8 empty] | 2 Char |  | ALL
BACnet Description 13 | 2646 | 42647 | BACnet Description 13 | [8 empty] | 2 Char |  | ALL
BACnet Description 14 | 2647 | 42648 | BACnet Description 14 | [8 empty] | 2 Char |  | ALL
BACnet Description 15 | 2648 | 42649 | BACnet Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
VERIS EMULATION LEGACY REGISTERS | - | - | VERIS EMULATION LEGACY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Veris Emulation Mode | 2200 | 42201 | Set to Veris Emulation Mode |  | Config | uint16 | R/W |  |  |  | system | 0-1 | 1 = Report Slave ID as Veris Model H8036 | ALL
kWh System LSW | 0 | 40001 | kWh System LSW | kWh | Veris | uint32 | R |  |  |  | element |  |  | ALL
kWh System MSW | 1 | 40002 | kWh System MSW | kWh | Veris |  | R |  |  |  | element |  |  | ALL
kW System | 2 | 40003 | kW System | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVAR System | 3 | 40004 | kVAR System | kVAR | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVA System | 4 | 40005 | kVA System | kVA | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF System | 5 | 40006 | Apparent PF System | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts Line to Line Avg | 6 | 40007 | Volts Line to Line Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts Line to Neutral Avg | 7 | 40008 | Volts Line to Neutral Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps System Avg | 8 | 40009 | Amps System Avg | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L1 | 9 | 40010 | kW L1 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L2 | 10 | 40011 | kW L2 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L3 | 11 | 40012 | kW L3 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L1 | 12 | 40013 | Apparent PF L1 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L2 | 13 | 40014 | Apparent PF L2 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L3 | 14 | 40015 | Apparent PF L3 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts L1 to L2 | 15 | 40016 | Volts L1 to L2 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to L3 | 16 | 40017 | Volts L2 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to L3 | 17 | 40018 | Volts L1 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to Neutral | 18 | 40019 | Volts L1 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to Neutral | 19 | 40020 | Volts L2 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L3 to Neutral | 20 | 40021 | Volts L3 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps L1 | 21 | 40022 | Amps L1 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L2 | 22 | 40023 | Amps L2 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L3 | 23 | 40024 | Amps L3 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW System Avg | 24 | 40025 | kW System Avg | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Now | 25 | 40026 | kW Demand Sys Now (was Min) | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Max | 26 | 40027 | kW Demand Sys Max | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL

## L
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS --> | 12
BACNET OBJECT FLOOR --> | 110000
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 | 41002 | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | 41003 | [8 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 | 41004 | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 | 41005 | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 | 41006 | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | 41007 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | 41008 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | 41009 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | 41010 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | 41011 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | 41012 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | 41013 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | 41014 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | 41015 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | 41016 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | 41017 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | 41018 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | 41019 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | 41020 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | 41021 | [8 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 | 41022 | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | 41023 | [8 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | 41024 | [8 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | 41025 | [8 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | 41026 | [8 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | 41027 | [8 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | 41028 | [8 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | 41029 | [8 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | 41030 | [8 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | 41031 | [8 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | 41032 | [8 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | 41033 | [8 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | 41034 | [8 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | 41035 | [8 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | 41036 | [8 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | 41037 | [8 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 | 41038 | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | 41039 | [8 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | 41040 | [8 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | 41041 | [8 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | 41042 | [8 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | 41043 | [8 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | 41044 | [8 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | 41045 | [8 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 | 41046 | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | 41047 | [8 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | 41048 | [8 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | 41049 | [8 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | 41050 | [8 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | 41051 | [8 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | 41052 | [8 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | 41053 | [8 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 | 41054 | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | 41055 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | 41056 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | 41057 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | 41058 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | 41059 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | 41060 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | 41061 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | 41062 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | 41063 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | 41064 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | 41065 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | 41066 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | 41067 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | 41068 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | 41069 | [8 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 | 41070 | Modbus Device Address |  |  | unit16 | R/W | 1069 | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | 41071 | [8 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 | 41072 | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 | 41073 | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 | 41074 | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | 41075 | [8 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | 41076 | [8 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | 41077 | [8 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 | 41078 | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 | 41079 | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 | 41080 | IP Address |  |  | string(8) | R/W | 1079 | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | 41081 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | 41082 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | 41083 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | 41084 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | 41085 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | 41086 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | 41087 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 | 41088 | Netmask |  |  | string(8) | R/W | 1087 | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | 41089 | [8 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | 41090 | [8 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | 41091 | [8 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | 41092 | [8 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | 41093 | [8 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | 41094 | [8 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | 41095 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 | 41096 | Gateway |  |  | string(8) | R/W | 1095 | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | 41097 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | 41098 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | 41099 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | 41100 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | 41101 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | 41102 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | 41103 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 | 41104 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | 41105 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | 41106 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | 41107 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | 41108 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | 41109 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | 41110 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | 41111 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 | 41112 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | 41113 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | 41114 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | 41115 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | 41116 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | 41117 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | 41118 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | 41119 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 | 41120 | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | 41121 | [8 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | 41122 | [8 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | 41123 | [8 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 | 41124 | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | 41125 | [9 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 | 41126 | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 | 41127 | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 | 41128 | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | 41129 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | 41130 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | 41131 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 | 41132 | Interface baud rate in bits per second |  |  | uint32 | R/W | 1131 | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | 41133 | [8 empty] | system |  |  | ALL
SERIAL BITS | 1133 | 41134 | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 | 41135 | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 | 41136 | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 | 41137 | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 | 41138 | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 | 41139 | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 | 41140 | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 | 41141 | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 | 41142 | Current Avg Element | A | Metrology | float32 | R | 111141 | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | 41143 | [8 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 | 41144 | Current CH1 (A) | A | Metrology | float32 | R | 111143 | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | 41145 | [8 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 | 41146 | Current CH2 (B) | A | Metrology | float32 | R | 111145 | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | 41147 | [8 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 | 41148 | Current CH3 (C) | A | Metrology | float32 | R | 111147 | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | 41149 | [8 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 | 41150 | Voltage L to N Avg Element | V | Metrology | float32 | R | 111149 | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | 41151 | [8 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 | 41152 | Voltage L1 to N (AN) | V | Metrology | float32 | R | 111151 | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | 41153 | [8 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 | 41154 | Voltage L2 to N (BN) | V | Metrology | float32 | R | 111153 | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | 41155 | [8 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 | 41156 | Voltage L3 to N (CN) | V | Metrology | float32 | R | 111155 | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | 41157 | [8 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 | 41158 | Voltage L to L Avg Element | V | Metrology | float32 | R | 111157 | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | 41159 | [8 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 | 41160 | Voltage L1 to L2 (AB) | V | Metrology | float32 | R | 111159 | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | 41161 | [8 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 | 41162 | Voltage L2 to L3 (BC) | V | Metrology | float32 | R | 111161 | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | 41163 | [8 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 | 41164 | Voltage L3 to L1 (CA) | V | Metrology | float32 | R | 111163 | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | 41165 | [8 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 | 41166 | Line Frequency | Hz | Metrology | float32 | R | 111165 | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | 41167 | [8 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 | 41168 | Power Sum Element | kW | Metrology | float32 | R | 111167 | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | 41169 | [8 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 | 41170 | Power CH1 (A) | kW | Metrology | float32 | R | 111169 | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | 41171 | [8 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 | 41172 | Power CH2 (B) | kW | Metrology | float32 | R | 111171 | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | 41173 | [8 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 | 41174 | Power CH3 (C) | kW | Metrology | float32 | R | 111173 | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | 41175 | [8 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 | 41176 | VA Sum Element | kVA | Metrology | float32 | R | 111175 | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | 41177 | [8 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 | 41178 | VA CH1 (A) | kVA | Metrology | float32 | R | 111177 | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | 41179 | [8 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 | 41180 | VA CH2 (B) | kVA | Metrology | float32 | R | 111179 | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | 41181 | [8 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 | 41182 | VA CH3 (C) | kVA | Metrology | float32 | R | 111181 | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | 41183 | [8 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 | 41184 | VAR Sum Element | kVAr | Metrology | float32 | R | 111183 | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | 41185 | [8 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 | 41186 | VAR CH1 (A) | kVAr | Metrology | float32 | R | 111185 | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | 41187 | [8 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 | 41188 | VAR CH2 (B) | kVAr | Metrology | float32 | R | 111187 | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | 41189 | [8 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 | 41190 | VAR CH3 (C) | kVAr | Metrology | float32 | R | 111189 | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | 41191 | [8 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 | 41192 | Apparent PF Avg Element | PF | Metrology | float32 | R | 111191 | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | 41193 | [8 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 | 41194 | Apparent PF CH1 (A) | PF | Metrology | float32 | R | 111193 | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | 41195 | [8 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 | 41196 | Apparent PF CH2 (B) | PF | Metrology | float32 | R | 111195 | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | 41197 | [8 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 | 41198 | Apparent PF CH3 ( C) | PF | Metrology | float32 | R | 111197 | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | 41199 | [8 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 | 41200 | Exported Energy Sum Element | kWh | Metrology | float32 | R | 111199 | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | 41201 | [8 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 | 41202 | Exported Energy CH1 (A) | kWh | Metrology | float32 | R | 111201 | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | 41203 | [8 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 | 41204 | Exported Energy CH2 (B) | kWh | Metrology | float32 | R | 111203 | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | 41205 | [8 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 | 41206 | Exported Energy CH3 (C) | kWh | Metrology | float32 | R | 111205 | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | 41207 | [8 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 | 41208 | Imported Energy Sum Element | kWh | Metrology | float32 | R | 111207 | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | 41209 | [8 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 | 41210 | Imported Energy CH1 (A) | kWh | Metrology | float32 | R | 111209 | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | 41211 | [8 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 | 41212 | Imported Energy CH2 (B) | kWh | Metrology | float32 | R | 111211 | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | 41213 | [8 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 | 41214 | Imported Energy CH3 (C) | kWh | Metrology | float32 | R | 111213 | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | 41215 | [8 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 | 41216 | Exported VAh Sum Element | kVAh | Metrology | float32 | R | 111215 | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | 41217 | [8 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 | 41218 | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R | 111217 | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | 41219 | [8 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 | 41220 | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R | 111219 | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | 41221 | [8 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 | 41222 | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R | 111221 | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | 41223 | [8 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 | 41224 | Imported VAh Sum Element | kVAh | Metrology | float32 | R | 111223 | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | 41225 | [8 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 | 41226 | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R | 111225 | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | 41227 | [8 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 | 41228 | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R | 111227 | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | 41229 | [8 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 | 41230 | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R | 111229 | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | 41231 | [8 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 | 41232 | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R | 111231 | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | 41233 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 | 41234 | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R | 111233 | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | 41235 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 | 41236 | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R | 111235 | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | 41237 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 | 41238 | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R | 111237 | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | 41239 | [8 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 | 41240 | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R | 111239 | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | 41241 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 | 41242 | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R | 111241 | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | 41243 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 | 41244 | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R | 111243 | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | 41245 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 | 41246 | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R | 111245 | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | 41247 | [8 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 | 41248 | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R | 111247 | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | 41249 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 | 41250 | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R | 111249 | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | 41251 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 | 41252 | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R | 111251 | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | 41253 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 | 41254 | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R | 111253 | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | 41255 | [8 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 | 41256 | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R | 111255 | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | 41257 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 | 41258 | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R | 111257 | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | 41259 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 | 41260 | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R | 111259 | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | 41261 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 | 41262 | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R | 111261 | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | 41263 | [8 empty] | element |  |  | ALL
Events MSW | 1263 | 41264 | Events MSW |  |  | bitfield32 | R | 1263 | AI | Events | system |  |  | ALL
Events LSW | 1264 | 41265 | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 | 41266 | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 | 41267 | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
FACTORY REGISTERS | - | - | FACTORY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Factory Unlock Register | 2000 | 42001 | Factory Unlock Register |  | Factory | unit16 | R/W |  |  |  | system |  | Reserved | ALL
Factory Reset | 2001 | 42002 | Factory Reset |  | Factory | unit16 | R/W |  |  |  | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
OEM Vendor ID | 2002 | 42003 | OEM Vendor ID |  | Factory | unit16 | R |  |  |  | system |  | Reserved | ALL
FACTORY_CONFIG | 2003 | 42004 | Factory Config |  | Factory | unit16 | R |  |  |  | system | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable | ALL
USER COMMAND POINTS | - | - | USER COMMAND POINTS | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 | 42101 | Reset (software) processor |  | User | unit16 | W | 2100 | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 | 42102 | Clear all accumulated measurements (CAM) |  | User | unit16 | W | 2101 | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 | 42103 | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W | 112102 | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 | 42104 | Clear Peak Demand Element |  | User | unit16 | W | 112103 | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 | 42105 | Clear Peak Demand All |  | User | unit16 | W | 2104 | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 | 42106 | Reset to User Defaults |  | User | unit16 | W | 2105 | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - | USER CONFIG POINTS | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 | 42202 | Sliding or Fixed |  | Config | enum16 | R | 2201 | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 | 42203 | Demand Window | Min | Config | uint16 | R | 2202 | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 | 42204 | Volt Multiplier VINPUT1 |  | Config | float32 | R/W | 2203 | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | 42205 | [8 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 | 42206 | Volt Multiplier VINPUT2 |  | Config | float32 | R/W | 2205 | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | 42207 | [8 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 | 42208 | Service Type |  | Config | enum16 | R/W | 112207 | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 | 42209 | Snap MV Threshold | PER | Config | float32 | R/W | 2208 | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | 42210 | [8 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 | 42211 | Snap Rog Threshold | PER | Config | float32 | R/W | 2210 | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | 42212 | [8 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 | 42213 | Snap Volt Threshold | V | Config | float32 | R/W | 2212 | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | 42214 | [8 empty] | system |  |  | ALL
Communications Mode | 2214 | 42215 | Communications Mode |  | Config |  |  | 2214 | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 | 42216 | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W | 2215 | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | 42217 | [8 empty] | system |  |  | ALL
Voltage Input Element | 2217 | 42218 | Element Voltage Input |  | Config | enum16 | R/W | 112217 | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 | 42219 | CT1 RANGE | A | Config | float32 | R/W | 112218 | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | 42220 | [8 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 | 42221 | Voltage Reference for CT1 |  | Config | enum16 | R/W | 112220 | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 | 42222 | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W | 112221 | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | 42223 | [8 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 | 42224 | CT1 TYPE |  | Config | enum16 | R/W | 112223 | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 | 42225 | CT1 PHASE SHIFT | Deg | Config | float32 | R/W | 112224 | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | 42226 | [8 empty] | element |  |  | ALL
CH1 CT Sign | 2226 | 42227 | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W | 112226 | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 | 42228 | CT2 RANGE | A | Config | float32 | R/W | 112227 | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | 42229 | [8 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 | 42230 | Voltage Reference for CT2 |  | Config | enum16 | R/W | 112229 | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 | 42231 | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W | 112230 | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | 42232 | [8 empty] | element | >0 |  | ALL
CH2 CT type | 2232 | 42233 | CT2 TYPE |  | Config | enum16 | R/W | 112232 | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 | 42234 | CT2 PHASE SHIFT | Deg | Config | float32 | R/W | 112233 | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | 42235 | [8 empty] | element |  |  | ALL
CH2 CT Sign | 2235 | 42236 | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W | 112235 | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 | 42237 | CT3 INTEGER | A | Config | float32 | R/W | 112236 | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | 42238 | [8 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 | 42239 | Voltage Reference for CT3 |  | Config | enum16 | R/W | 112238 | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 | 42240 | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W | 112239 | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | 42241 | [8 empty] | element | >0 |  | ALL
CH3 CT type | 2241 | 42242 | CT3 TYPE |  | Config | enum16 | R/W | 112241 | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 | 42243 | CT3 PHASE SHIFT | Deg | Config | float32 | R/W | 112242 | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | 42244 | [8 empty] | element |  |  | ALL
CH3 CT Sign | 2244 | 42245 | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W | 112244 | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 | 42246 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 | 42247 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 | 42248 | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 | 42249 | PF Sign Convention |  | Config | uint16 | R/W | 2248 | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 | 42250 | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 | 42251 | BACnet UDP Port |  | Config | uint16 | R/W | 2250 | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 | 42252 | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 | 42253 | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | 42254 | [8 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 | 42261 | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | 42262 | [11 empty] | ALL
BACnet Max Info Frames | 2262 | 42263 | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 | 42264 | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 | 42265 | BBMD IP Address |  | Config | string(16) | R/W | 2264 | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | 42266 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | 42267 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | 42268 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | 42269 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | 42270 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | 42271 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | 42272 | [9 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 | 42273 | LCD/WebApp Read Password |  | Config | uint16 | R/W | 2272 | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 | 42274 | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 | 42275 | Customer Line frequency |  | Config | float | R/W | 2274 | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | 42276 | [10 empty] | Reserved | ALL
Communications Interface Configured | 2276 | 42277 | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 | 42278 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 | 42279 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 | 42280 | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 | 42281 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 | 42282 | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 | 42283 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 | 42284 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 | 42285 | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 | 42286 | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 | 42287 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 | 42288 | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 | 42289 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 | 42290 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 | 42291 | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 | 42292 | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | 42293 | [11 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 | 42294 | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | 42295 | [11 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 | 42296 | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 | 42297 | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - | METROLOGY POINTS | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 | 42301 | Displacement PF Avg Element | dPF | Metrology | float32 | R | 112300 | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | 42302 | [11 empty] | ALL
Displacement PF CH1 (MSW) | 2302 | 42303 | Displacement PF CH1 (A) | dPF | Metrology | float32 | R | 112302 | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | 42304 | [11 empty] | ALL
Displacement PF CH2 (MSW) | 2304 | 42305 | Displacement PF CH2 (B) | dPF | Metrology | float32 | R | 112304 | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | 42306 | [11 empty] | ALL
Displacement PF CH3 (MSW) | 2306 | 42307 | Displacement PF CH3 (C) | dPF | Metrology | float32 | R | 112306 | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | 42308 | [11 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 | 42309 | Avg Apparent PF Element | aPF | Metrology | float32 | R | 112308 | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | 42310 | [11 empty] | ALL
Apparent PF CH1 (MSW) | 2310 | 42311 | Apparent PF CH1 (A) | aPF | Metrology | float32 | R | 112310 | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | 42312 | [11 empty] | ALL
Apparent PF CH2 (MSW) | 2312 | 42313 | Apparent PF CH2 (B) | aPF | Metrology | float32 | R | 112312 | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | 42314 | [11 empty] | ALL
Apparent PF CH3 (MSW) | 2314 | 42315 | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R | 112314 | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | 42316 | [11 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 | 42317 | Distortion PF Avg Element | tPF | Metrology | float32 | R | 112316 | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | 42318 | [11 empty] | ALL
Distortion PF CH1 (MSW) | 2318 | 42319 | Distortion PF CH1 (A) | tPF | Metrology | float32 | R | 112318 | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | 42320 | [11 empty] | ALL
Distortion PF CH2 (MSW) | 2320 | 42321 | Distortion PF CH2 (B) | tPF | Metrology | float32 | R | 112320 | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | 42322 | [11 empty] | ALL
Distortion PF CH3 (MSW) | 2322 | 42323 | Distortion PF CH3 (C) | tPF | Metrology | float32 | R | 112322 | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | 42324 | [11 empty] | ALL
THD Avg Element (MSW) | 2324 | 42325 | THD Avg Element | % | Metrology | float32 | R | 112324 | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | 42326 | [11 empty] | ALL
THD CH1 (MSW) | 2326 | 42327 | THD CH1 (A) | % | Metrology | float32 | R | 112326 | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | 42328 | [11 empty] | ALL
THD CH2 (MSW) | 2328 | 42329 | THD CH2 (B) | % | Metrology | float32 | R | 112328 | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | 42330 | [11 empty] | ALL
THD CH3 (MSW) | 2330 | 42331 | THD CH3 (C) | % | Metrology | float32 | R | 112330 | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | 42332 | [11 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 | 42333 | Power Demand Max Interval Element | kW | Metrology | float32 | R | 112332 | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | 42334 | [11 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 | 42335 | Power Demand This Interval Element | kW | Metrology | float32 | R | 112334 | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | 42336 | [11 empty] | ALL
VA Peak Demand Element (MSW) | 2336 | 42337 | VA Demand Max Interval Element | kVA | Metrology | float32 | R | 112336 | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | 42338 | [11 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 | 42339 | VA Demand This Interval Element | kVA | Metrology | float32 | R | 112338 | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | 42340 | [11 empty] | ALL
Not Used | 2340 | 42341 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 | 42342 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 | 42343 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 | 42344 | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 | 42345 | Energy Net Sum Element | kWh | Metrology | float32 | R | 112344 | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | 42346 | [8 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 | 42347 | Energy Net CH1 | kWh | Metrology | float32 | R | 112346 | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | 42348 | [8 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 | 42349 | Energy Net CH2 | kWh | Metrology | float32 | R | 112348 | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | 42350 | [8 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 | 42351 | Energy Net CH3 | kWh | Metrology | float32 | R | 112350 | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | 42352 | [8 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 | 42353 | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R | 112352 | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | 42354 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 | 42355 | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R | 112354 | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | 42356 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 | 42357 | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R | 112356 | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | 42358 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 | 42359 | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R | 112358 | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | 42360 | [8 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 | 42361 | VARh Net Sum Element | kVArh | Metrology | float32 | R | 112360 | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | 42362 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 | 42363 | VARh Net CH1 | kVArh | Metrology | float32 | R | 112362 | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | 42364 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 | 42365 | VARh Net CH2 | kVArh | Metrology | float32 | R | 112364 | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | 42366 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 | 42367 | VARh Net CH3 | kVArh | Metrology | float32 | R | 112366 | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | 42368 | [8 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 | 42369 | Time Since Reset MSW | Sec | Metrology | uint32 |  | 2368 | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 | 42370 | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 | 42371 | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 | 42372 | CH1 Angle | Deg | Metrology | float32 | R | 112371 | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | 42373 | [8 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 | 42374 | CH2 Angle | Deg | Metrology | float32 | R | 112373 | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | 42375 | [8 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 | 42376 | CH3 Angle | Deg | Metrology | float32 | R | 112375 | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | 42377 | [11 empty] | ALL
Phase Chek System Status | 2377 | 42378 | System Phase Check Status |  | Metrology | bitfield16 | R | 2377 | BV | Phase Check System Status | system | 0,1 | 0 (All Channels OK), 1(Somewhere a channel is reading a dPF < 0.55), check register 2378 for each Element | ALL
Phase Chek Element Status | 2378 | 42379 | Element Phase Check Status |  | Metrology | bitfield16 | R | 112378 | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 | 42380 | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 | 42381 | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 | 42382 | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 | 42392 | Element Angle |  | Metrology | float | R | 112391 | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | 42393 | [11 empty] | ALL
PULSE INPUTS | - | - | PULSE INPUTS | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 | 42401 | Pulse Input 1 Enable |  | Config | uint16 | R/W | 2400 | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 | 42402 | Pulse Input 1 Scale Factor |  | Config | float32 | R/W | 2401 | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 | 42403 |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 | 42404 | Pulse Input 1 Units |  | Config | string(4) | R/W | 2403 | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 | 42405 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 | 42406 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 | 42407 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 | 42408 | Pulse Input 1 Accumulator |  | Metrology | float32 | R | 2407 | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | 42409 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 | 42410 | Pulse Input 1 Accumulator Clear |  | User | unit16 | W | 2409 | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 | 42411 | Pulse Input 2 Enable |  | Config | uint16 | R/W | 2410 | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 | 42412 | Pulse Input 2 Scale Factor |  | Config | float32 | R/W | 2411 | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | 42413 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 | 42414 | Pulse Input 2 Units |  | Config | string(4) | R/W | 2413 | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 | 42415 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 | 42416 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 | 42417 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 | 42418 | Pulse Input 2 Accumulator |  | Metrology | float32 | R | 2417 | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | 42419 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 | 42420 | Pulse Input 2 Accumulator Clear |  | User | unit16 | W | 2419 | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 | 42421 | Pulse Input 3 Enable |  | Config | uint16 | R/W | 2420 | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 | 42422 | Pulse Input 3 Scale Factor |  | Config | float32 | R/W | 2421 | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | 42423 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 | 42424 | Pulse Input 3 Units |  | Config | string(4) | R/W | 2423 | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 | 42425 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 | 42426 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 | 42427 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 | 42428 | Pulse Input 3 Accumulator |  | Metrology | float32 | R | 2427 | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | 42429 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 | 42430 | Pulse Input 3 Accumulator Clear |  | User |  | W | 2429 | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 | 42431 | Pulse Input 4 Enable |  | Config | uint16 | R/W | 2430 | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 | 42432 | Pulse Input 4 Scale Factor |  | Config | float32 | R/W | 2431 | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | 42433 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 | 42434 | Pulse Input 4 Units |  | Config | string(4) | R/W | 2433 | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 | 42435 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 | 42436 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 | 42437 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 | 42438 | Pulse Input 4 Accumulator |  | Metrology | float32 | R | 2437 | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | 42439 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 | 42440 | Pulse Input 4 Accumulator Clear |  | User | unit16 | W | 2439 | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - | ALARMS | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 | 42452 | State of Alarm |  | Metrology | uint16 | R/W | 2451 | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 | 42453 | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 | 42454 | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 | 42455 | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 | 42456 | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 | 42457 | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 | 42458 | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 | 42459 | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W | 2458 | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 | 42460 | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W | 2459 | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Range Vin1 L1N Under | 2460 | 42461 | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W | 2460 | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 | 42462 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2N Under | 2462 | 42463 | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W | 2462 | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 | 42464 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3N Under | 2464 | 42465 | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W | 2464 | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 | 42466 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L1L2 Under | 2466 | 42467 | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W | 2466 | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 | 42468 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2L3 Under | 2468 | 42469 | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W | 2468 | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 | 42470 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3L1 Under | 2470 | 42471 | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W | 2470 | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 | 42472 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin2 L1N Under | 2472 | 42473 | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W | 2472 | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 | 42474 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2N Under | 2474 | 42475 | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W | 2474 | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 | 42476 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3N Under | 2476 | 42477 | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W | 2476 | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 | 42478 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L1L2 Under | 2478 | 42479 | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W | 2478 | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 | 42480 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2L3 Under | 2480 | 42481 | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W | 2480 | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 | 42482 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3L1 Under | 2482 | 42483 | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W | 2482 | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 | 42484 | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 | 42485 | Voltage Alarm Persistence | Sec | Config | uint16 | R/W | 2484 | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 | 42486 | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R | 2485 | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 | 42487 | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 | 42488 | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R | 2487 | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 | 42489 | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 | 42490 | Real Time Clock MSW |  | Config | uint16 | R/W | 2489 | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 | 42491 | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - | USER CONFIG POINTS 2 | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 | 42602 | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 | 42603 | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 | 42604 | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 | 42605 | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 | 42606 | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 | 42607 | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 | 42608 | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 | 42609 | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 | 42610 | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 | 42611 | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 | 42612 | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 | 42613 | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 | 42614 | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 | 42615 | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 | 42616 | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 | 42617 | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 | 42618 | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 | 42619 | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 | 42620 | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 | 42621 | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 | 42622 | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 | 42623 | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 | 42624 | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 | 42625 | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 | 42626 | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 | 42627 | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 | 42628 | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 | 42629 | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 | 42630 | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 | 42631 | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 | 42632 | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 | 42633 | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 | 42634 | BACnet Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | 2634 | 42635 | BACnet Description 1 | [8 empty] | 2 Char |  | ALL
BACnet Description 2 | 2635 | 42636 | BACnet Description 2 | [8 empty] | 2 Char |  | ALL
BACnet Description 3 | 2636 | 42637 | BACnet Description 3 | [8 empty] | 2 Char |  | ALL
BACnet Description 4 | 2637 | 42638 | BACnet Description 4 | [8 empty] | 2 Char |  | ALL
BACnet Description 5 | 2638 | 42639 | BACnet Description 5 | [8 empty] | 2 Char |  | ALL
BACnet Description 6 | 2639 | 42640 | BACnet Description 6 | [8 empty] | 2 Char |  | ALL
BACnet Description 7 | 2640 | 42641 | BACnet Description 7 | [8 empty] | 2 Char |  | ALL
BACnet Description 8 | 2641 | 42642 | BACnet Description 8 | [8 empty] | 2 Char |  | ALL
BACnet Description 9 | 2642 | 42643 | BACnet Description 9 | [8 empty] | 2 Char |  | ALL
BACnet Description 10 | 2643 | 42644 | BACnet Description 10 | [8 empty] | 2 Char |  | ALL
BACnet Description 11 | 2644 | 42645 | BACnet Description 11 | [8 empty] | 2 Char |  | ALL
BACnet Description 12 | 2645 | 42646 | BACnet Description 12 | [8 empty] | 2 Char |  | ALL
BACnet Description 13 | 2646 | 42647 | BACnet Description 13 | [8 empty] | 2 Char |  | ALL
BACnet Description 14 | 2647 | 42648 | BACnet Description 14 | [8 empty] | 2 Char |  | ALL
BACnet Description 15 | 2648 | 42649 | BACnet Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
VERIS EMULATION LEGACY REGISTERS | - | - | VERIS EMULATION LEGACY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Veris Emulation Mode | 2200 | 42201 | Set to Veris Emulation Mode |  | Config | uint16 | R/W |  |  |  | system | 0-1 | 1 = Report Slave ID as Veris Model H8036 | ALL
kWh System LSW | 0 | 40001 | kWh System LSW | kWh | Veris | uint32 | R |  |  |  | element |  |  | ALL
kWh System MSW | 1 | 40002 | kWh System MSW | kWh | Veris |  | R |  |  |  | element |  |  | ALL
kW System | 2 | 40003 | kW System | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVAR System | 3 | 40004 | kVAR System | kVAR | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVA System | 4 | 40005 | kVA System | kVA | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF System | 5 | 40006 | Apparent PF System | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts Line to Line Avg | 6 | 40007 | Volts Line to Line Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts Line to Neutral Avg | 7 | 40008 | Volts Line to Neutral Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps System Avg | 8 | 40009 | Amps System Avg | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L1 | 9 | 40010 | kW L1 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L2 | 10 | 40011 | kW L2 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L3 | 11 | 40012 | kW L3 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L1 | 12 | 40013 | Apparent PF L1 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L2 | 13 | 40014 | Apparent PF L2 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L3 | 14 | 40015 | Apparent PF L3 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts L1 to L2 | 15 | 40016 | Volts L1 to L2 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to L3 | 16 | 40017 | Volts L2 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to L3 | 17 | 40018 | Volts L1 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to Neutral | 18 | 40019 | Volts L1 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to Neutral | 19 | 40020 | Volts L2 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L3 to Neutral | 20 | 40021 | Volts L3 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps L1 | 21 | 40022 | Amps L1 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L2 | 22 | 40023 | Amps L2 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L3 | 23 | 40024 | Amps L3 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW System Avg | 24 | 40025 | kW System Avg | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Now | 25 | 40026 | kW Demand Sys Now (was Min) | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Max | 26 | 40027 | kW Demand Sys Max | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL

## M
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS --> | 13
BACNET OBJECT FLOOR --> | 120000
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 | 41002 | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | 41003 | [8 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 | 41004 | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 | 41005 | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 | 41006 | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | 41007 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | 41008 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | 41009 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | 41010 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | 41011 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | 41012 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | 41013 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | 41014 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | 41015 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | 41016 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | 41017 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | 41018 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | 41019 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | 41020 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | 41021 | [8 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 | 41022 | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | 41023 | [8 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | 41024 | [8 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | 41025 | [8 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | 41026 | [8 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | 41027 | [8 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | 41028 | [8 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | 41029 | [8 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | 41030 | [8 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | 41031 | [8 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | 41032 | [8 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | 41033 | [8 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | 41034 | [8 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | 41035 | [8 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | 41036 | [8 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | 41037 | [8 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 | 41038 | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | 41039 | [8 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | 41040 | [8 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | 41041 | [8 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | 41042 | [8 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | 41043 | [8 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | 41044 | [8 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | 41045 | [8 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 | 41046 | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | 41047 | [8 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | 41048 | [8 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | 41049 | [8 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | 41050 | [8 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | 41051 | [8 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | 41052 | [8 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | 41053 | [8 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 | 41054 | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | 41055 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | 41056 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | 41057 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | 41058 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | 41059 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | 41060 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | 41061 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | 41062 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | 41063 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | 41064 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | 41065 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | 41066 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | 41067 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | 41068 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | 41069 | [8 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 | 41070 | Modbus Device Address |  |  | unit16 | R/W | 1069 | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | 41071 | [8 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 | 41072 | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 | 41073 | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 | 41074 | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | 41075 | [8 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | 41076 | [8 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | 41077 | [8 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 | 41078 | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 | 41079 | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 | 41080 | IP Address |  |  | string(8) | R/W | 1079 | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | 41081 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | 41082 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | 41083 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | 41084 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | 41085 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | 41086 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | 41087 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 | 41088 | Netmask |  |  | string(8) | R/W | 1087 | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | 41089 | [8 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | 41090 | [8 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | 41091 | [8 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | 41092 | [8 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | 41093 | [8 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | 41094 | [8 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | 41095 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 | 41096 | Gateway |  |  | string(8) | R/W | 1095 | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | 41097 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | 41098 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | 41099 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | 41100 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | 41101 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | 41102 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | 41103 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 | 41104 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | 41105 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | 41106 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | 41107 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | 41108 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | 41109 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | 41110 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | 41111 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 | 41112 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | 41113 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | 41114 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | 41115 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | 41116 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | 41117 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | 41118 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | 41119 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 | 41120 | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | 41121 | [8 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | 41122 | [8 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | 41123 | [8 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 | 41124 | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | 41125 | [9 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 | 41126 | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 | 41127 | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 | 41128 | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | 41129 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | 41130 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | 41131 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 | 41132 | Interface baud rate in bits per second |  |  | uint32 | R/W | 1131 | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | 41133 | [8 empty] | system |  |  | ALL
SERIAL BITS | 1133 | 41134 | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 | 41135 | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 | 41136 | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 | 41137 | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 | 41138 | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 | 41139 | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 | 41140 | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 | 41141 | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 | 41142 | Current Avg Element | A | Metrology | float32 | R | 121141 | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | 41143 | [8 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 | 41144 | Current CH1 (A) | A | Metrology | float32 | R | 121143 | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | 41145 | [8 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 | 41146 | Current CH2 (B) | A | Metrology | float32 | R | 121145 | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | 41147 | [8 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 | 41148 | Current CH3 (C) | A | Metrology | float32 | R | 121147 | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | 41149 | [8 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 | 41150 | Voltage L to N Avg Element | V | Metrology | float32 | R | 121149 | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | 41151 | [8 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 | 41152 | Voltage L1 to N (AN) | V | Metrology | float32 | R | 121151 | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | 41153 | [8 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 | 41154 | Voltage L2 to N (BN) | V | Metrology | float32 | R | 121153 | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | 41155 | [8 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 | 41156 | Voltage L3 to N (CN) | V | Metrology | float32 | R | 121155 | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | 41157 | [8 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 | 41158 | Voltage L to L Avg Element | V | Metrology | float32 | R | 121157 | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | 41159 | [8 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 | 41160 | Voltage L1 to L2 (AB) | V | Metrology | float32 | R | 121159 | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | 41161 | [8 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 | 41162 | Voltage L2 to L3 (BC) | V | Metrology | float32 | R | 121161 | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | 41163 | [8 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 | 41164 | Voltage L3 to L1 (CA) | V | Metrology | float32 | R | 121163 | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | 41165 | [8 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 | 41166 | Line Frequency | Hz | Metrology | float32 | R | 121165 | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | 41167 | [8 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 | 41168 | Power Sum Element | kW | Metrology | float32 | R | 121167 | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | 41169 | [8 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 | 41170 | Power CH1 (A) | kW | Metrology | float32 | R | 121169 | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | 41171 | [8 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 | 41172 | Power CH2 (B) | kW | Metrology | float32 | R | 121171 | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | 41173 | [8 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 | 41174 | Power CH3 (C) | kW | Metrology | float32 | R | 121173 | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | 41175 | [8 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 | 41176 | VA Sum Element | kVA | Metrology | float32 | R | 121175 | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | 41177 | [8 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 | 41178 | VA CH1 (A) | kVA | Metrology | float32 | R | 121177 | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | 41179 | [8 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 | 41180 | VA CH2 (B) | kVA | Metrology | float32 | R | 121179 | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | 41181 | [8 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 | 41182 | VA CH3 (C) | kVA | Metrology | float32 | R | 121181 | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | 41183 | [8 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 | 41184 | VAR Sum Element | kVAr | Metrology | float32 | R | 121183 | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | 41185 | [8 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 | 41186 | VAR CH1 (A) | kVAr | Metrology | float32 | R | 121185 | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | 41187 | [8 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 | 41188 | VAR CH2 (B) | kVAr | Metrology | float32 | R | 121187 | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | 41189 | [8 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 | 41190 | VAR CH3 (C) | kVAr | Metrology | float32 | R | 121189 | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | 41191 | [8 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 | 41192 | Apparent PF Avg Element | PF | Metrology | float32 | R | 121191 | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | 41193 | [8 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 | 41194 | Apparent PF CH1 (A) | PF | Metrology | float32 | R | 121193 | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | 41195 | [8 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 | 41196 | Apparent PF CH2 (B) | PF | Metrology | float32 | R | 121195 | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | 41197 | [8 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 | 41198 | Apparent PF CH3 ( C) | PF | Metrology | float32 | R | 121197 | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | 41199 | [8 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 | 41200 | Exported Energy Sum Element | kWh | Metrology | float32 | R | 121199 | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | 41201 | [8 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 | 41202 | Exported Energy CH1 (A) | kWh | Metrology | float32 | R | 121201 | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | 41203 | [8 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 | 41204 | Exported Energy CH2 (B) | kWh | Metrology | float32 | R | 121203 | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | 41205 | [8 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 | 41206 | Exported Energy CH3 (C) | kWh | Metrology | float32 | R | 121205 | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | 41207 | [8 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 | 41208 | Imported Energy Sum Element | kWh | Metrology | float32 | R | 121207 | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | 41209 | [8 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 | 41210 | Imported Energy CH1 (A) | kWh | Metrology | float32 | R | 121209 | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | 41211 | [8 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 | 41212 | Imported Energy CH2 (B) | kWh | Metrology | float32 | R | 121211 | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | 41213 | [8 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 | 41214 | Imported Energy CH3 (C) | kWh | Metrology | float32 | R | 121213 | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | 41215 | [8 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 | 41216 | Exported VAh Sum Element | kVAh | Metrology | float32 | R | 121215 | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | 41217 | [8 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 | 41218 | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R | 121217 | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | 41219 | [8 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 | 41220 | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R | 121219 | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | 41221 | [8 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 | 41222 | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R | 121221 | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | 41223 | [8 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 | 41224 | Imported VAh Sum Element | kVAh | Metrology | float32 | R | 121223 | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | 41225 | [8 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 | 41226 | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R | 121225 | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | 41227 | [8 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 | 41228 | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R | 121227 | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | 41229 | [8 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 | 41230 | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R | 121229 | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | 41231 | [8 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 | 41232 | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R | 121231 | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | 41233 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 | 41234 | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R | 121233 | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | 41235 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 | 41236 | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R | 121235 | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | 41237 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 | 41238 | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R | 121237 | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | 41239 | [8 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 | 41240 | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R | 121239 | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | 41241 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 | 41242 | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R | 121241 | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | 41243 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 | 41244 | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R | 121243 | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | 41245 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 | 41246 | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R | 121245 | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | 41247 | [8 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 | 41248 | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R | 121247 | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | 41249 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 | 41250 | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R | 121249 | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | 41251 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 | 41252 | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R | 121251 | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | 41253 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 | 41254 | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R | 121253 | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | 41255 | [8 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 | 41256 | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R | 121255 | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | 41257 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 | 41258 | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R | 121257 | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | 41259 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 | 41260 | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R | 121259 | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | 41261 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 | 41262 | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R | 121261 | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | 41263 | [8 empty] | element |  |  | ALL
Events MSW | 1263 | 41264 | Events MSW |  |  | bitfield32 | R | 1263 | AI | Events | system |  |  | ALL
Events LSW | 1264 | 41265 | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 | 41266 | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 | 41267 | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
FACTORY REGISTERS | - | - | FACTORY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Factory Unlock Register | 2000 | 42001 | Factory Unlock Register |  | Factory | unit16 | R/W |  |  |  | system |  | Reserved | ALL
Factory Reset | 2001 | 42002 | Factory Reset |  | Factory | unit16 | R/W |  |  |  | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
OEM Vendor ID | 2002 | 42003 | OEM Vendor ID |  | Factory | unit16 | R |  |  |  | system |  | Reserved | ALL
FACTORY_CONFIG | 2003 | 42004 | Factory Config |  | Factory | unit16 | R |  |  |  | system | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable | ALL
USER COMMAND POINTS | - | - | USER COMMAND POINTS | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 | 42101 | Reset (software) processor |  | User | unit16 | W | 2100 | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 | 42102 | Clear all accumulated measurements (CAM) |  | User | unit16 | W | 2101 | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 | 42103 | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W | 122102 | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 | 42104 | Clear Peak Demand Element |  | User | unit16 | W | 122103 | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 | 42105 | Clear Peak Demand All |  | User | unit16 | W | 2104 | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 | 42106 | Reset to User Defaults |  | User | unit16 | W | 2105 | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - | USER CONFIG POINTS | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 | 42202 | Sliding or Fixed |  | Config | enum16 | R | 2201 | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 | 42203 | Demand Window | Min | Config | uint16 | R | 2202 | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 | 42204 | Volt Multiplier VINPUT1 |  | Config | float32 | R/W | 2203 | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | 42205 | [8 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 | 42206 | Volt Multiplier VINPUT2 |  | Config | float32 | R/W | 2205 | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | 42207 | [8 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 | 42208 | Service Type |  | Config | enum16 | R/W | 122207 | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 | 42209 | Snap MV Threshold | PER | Config | float32 | R/W | 2208 | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | 42210 | [8 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 | 42211 | Snap Rog Threshold | PER | Config | float32 | R/W | 2210 | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | 42212 | [8 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 | 42213 | Snap Volt Threshold | V | Config | float32 | R/W | 2212 | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | 42214 | [8 empty] | system |  |  | ALL
Communications Mode | 2214 | 42215 | Communications Mode |  | Config |  |  | 2214 | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 | 42216 | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W | 2215 | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | 42217 | [8 empty] | system |  |  | ALL
Voltage Input Element | 2217 | 42218 | Element Voltage Input |  | Config | enum16 | R/W | 122217 | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 | 42219 | CT1 RANGE | A | Config | float32 | R/W | 122218 | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | 42220 | [8 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 | 42221 | Voltage Reference for CT1 |  | Config | enum16 | R/W | 122220 | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 | 42222 | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W | 122221 | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | 42223 | [8 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 | 42224 | CT1 TYPE |  | Config | enum16 | R/W | 122223 | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 | 42225 | CT1 PHASE SHIFT | Deg | Config | float32 | R/W | 122224 | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | 42226 | [8 empty] | element |  |  | ALL
CH1 CT Sign | 2226 | 42227 | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W | 122226 | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 | 42228 | CT2 RANGE | A | Config | float32 | R/W | 122227 | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | 42229 | [8 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 | 42230 | Voltage Reference for CT2 |  | Config | enum16 | R/W | 122229 | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 | 42231 | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W | 122230 | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | 42232 | [8 empty] | element | >0 |  | ALL
CH2 CT type | 2232 | 42233 | CT2 TYPE |  | Config | enum16 | R/W | 122232 | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 | 42234 | CT2 PHASE SHIFT | Deg | Config | float32 | R/W | 122233 | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | 42235 | [8 empty] | element |  |  | ALL
CH2 CT Sign | 2235 | 42236 | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W | 122235 | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 | 42237 | CT3 INTEGER | A | Config | float32 | R/W | 122236 | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | 42238 | [8 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 | 42239 | Voltage Reference for CT3 |  | Config | enum16 | R/W | 122238 | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 | 42240 | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W | 122239 | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | 42241 | [8 empty] | element | >0 |  | ALL
CH3 CT type | 2241 | 42242 | CT3 TYPE |  | Config | enum16 | R/W | 122241 | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 | 42243 | CT3 PHASE SHIFT | Deg | Config | float32 | R/W | 122242 | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | 42244 | [8 empty] | element |  |  | ALL
CH3 CT Sign | 2244 | 42245 | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W | 122244 | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 | 42246 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 | 42247 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 | 42248 | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 | 42249 | PF Sign Convention |  | Config | uint16 | R/W | 2248 | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 | 42250 | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 | 42251 | BACnet UDP Port |  | Config | uint16 | R/W | 2250 | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 | 42252 | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 | 42253 | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | 42254 | [8 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 | 42261 | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | 42262 | [11 empty] | ALL
BACnet Max Info Frames | 2262 | 42263 | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 | 42264 | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 | 42265 | BBMD IP Address |  | Config | string(16) | R/W | 2264 | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | 42266 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | 42267 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | 42268 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | 42269 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | 42270 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | 42271 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | 42272 | [9 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 | 42273 | LCD/WebApp Read Password |  | Config | uint16 | R/W | 2272 | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 | 42274 | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 | 42275 | Customer Line frequency |  | Config | float | R/W | 2274 | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | 42276 | [10 empty] | Reserved | ALL
Communications Interface Configured | 2276 | 42277 | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 | 42278 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 | 42279 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 | 42280 | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 | 42281 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 | 42282 | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 | 42283 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 | 42284 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 | 42285 | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 | 42286 | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 | 42287 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 | 42288 | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 | 42289 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 | 42290 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 | 42291 | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 | 42292 | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | 42293 | [11 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 | 42294 | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | 42295 | [11 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 | 42296 | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 | 42297 | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - | METROLOGY POINTS | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 | 42301 | Displacement PF Avg Element | dPF | Metrology | float32 | R | 122300 | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | 42302 | [11 empty] | ALL
Displacement PF CH1 (MSW) | 2302 | 42303 | Displacement PF CH1 (A) | dPF | Metrology | float32 | R | 122302 | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | 42304 | [11 empty] | ALL
Displacement PF CH2 (MSW) | 2304 | 42305 | Displacement PF CH2 (B) | dPF | Metrology | float32 | R | 122304 | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | 42306 | [11 empty] | ALL
Displacement PF CH3 (MSW) | 2306 | 42307 | Displacement PF CH3 (C) | dPF | Metrology | float32 | R | 122306 | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | 42308 | [11 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 | 42309 | Avg Apparent PF Element | aPF | Metrology | float32 | R | 122308 | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | 42310 | [11 empty] | ALL
Apparent PF CH1 (MSW) | 2310 | 42311 | Apparent PF CH1 (A) | aPF | Metrology | float32 | R | 122310 | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | 42312 | [11 empty] | ALL
Apparent PF CH2 (MSW) | 2312 | 42313 | Apparent PF CH2 (B) | aPF | Metrology | float32 | R | 122312 | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | 42314 | [11 empty] | ALL
Apparent PF CH3 (MSW) | 2314 | 42315 | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R | 122314 | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | 42316 | [11 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 | 42317 | Distortion PF Avg Element | tPF | Metrology | float32 | R | 122316 | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | 42318 | [11 empty] | ALL
Distortion PF CH1 (MSW) | 2318 | 42319 | Distortion PF CH1 (A) | tPF | Metrology | float32 | R | 122318 | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | 42320 | [11 empty] | ALL
Distortion PF CH2 (MSW) | 2320 | 42321 | Distortion PF CH2 (B) | tPF | Metrology | float32 | R | 122320 | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | 42322 | [11 empty] | ALL
Distortion PF CH3 (MSW) | 2322 | 42323 | Distortion PF CH3 (C) | tPF | Metrology | float32 | R | 122322 | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | 42324 | [11 empty] | ALL
THD Avg Element (MSW) | 2324 | 42325 | THD Avg Element | % | Metrology | float32 | R | 122324 | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | 42326 | [11 empty] | ALL
THD CH1 (MSW) | 2326 | 42327 | THD CH1 (A) | % | Metrology | float32 | R | 122326 | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | 42328 | [11 empty] | ALL
THD CH2 (MSW) | 2328 | 42329 | THD CH2 (B) | % | Metrology | float32 | R | 122328 | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | 42330 | [11 empty] | ALL
THD CH3 (MSW) | 2330 | 42331 | THD CH3 (C) | % | Metrology | float32 | R | 122330 | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | 42332 | [11 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 | 42333 | Power Demand Max Interval Element | kW | Metrology | float32 | R | 122332 | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | 42334 | [11 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 | 42335 | Power Demand This Interval Element | kW | Metrology | float32 | R | 122334 | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | 42336 | [11 empty] | ALL
VA Peak Demand Element (MSW) | 2336 | 42337 | VA Demand Max Interval Element | kVA | Metrology | float32 | R | 122336 | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | 42338 | [11 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 | 42339 | VA Demand This Interval Element | kVA | Metrology | float32 | R | 122338 | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | 42340 | [11 empty] | ALL
Not Used | 2340 | 42341 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 | 42342 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 | 42343 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 | 42344 | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 | 42345 | Energy Net Sum Element | kWh | Metrology | float32 | R | 122344 | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | 42346 | [8 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 | 42347 | Energy Net CH1 | kWh | Metrology | float32 | R | 122346 | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | 42348 | [8 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 | 42349 | Energy Net CH2 | kWh | Metrology | float32 | R | 122348 | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | 42350 | [8 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 | 42351 | Energy Net CH3 | kWh | Metrology | float32 | R | 122350 | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | 42352 | [8 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 | 42353 | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R | 122352 | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | 42354 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 | 42355 | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R | 122354 | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | 42356 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 | 42357 | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R | 122356 | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | 42358 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 | 42359 | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R | 122358 | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | 42360 | [8 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 | 42361 | VARh Net Sum Element | kVArh | Metrology | float32 | R | 122360 | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | 42362 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 | 42363 | VARh Net CH1 | kVArh | Metrology | float32 | R | 122362 | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | 42364 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 | 42365 | VARh Net CH2 | kVArh | Metrology | float32 | R | 122364 | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | 42366 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 | 42367 | VARh Net CH3 | kVArh | Metrology | float32 | R | 122366 | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | 42368 | [8 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 | 42369 | Time Since Reset MSW | Sec | Metrology | uint32 |  | 2368 | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 | 42370 | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 | 42371 | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 | 42372 | CH1 Angle | Deg | Metrology | float32 | R | 122371 | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | 42373 | [8 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 | 42374 | CH2 Angle | Deg | Metrology | float32 | R | 122373 | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | 42375 | [8 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 | 42376 | CH3 Angle | Deg | Metrology | float32 | R | 122375 | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | 42377 | [11 empty] | ALL
Phase Chek System Status | 2377 | 42378 | System Phase Check Status |  | Metrology | bitfield16 | R | 2377 | BV | Phase Check System Status | system | 0,1 | 0 (All Channels OK), 1(Somewhere a channel is reading a dPF < 0.55), check register 2378 for each Element | ALL
Phase Chek Element Status | 2378 | 42379 | Element Phase Check Status |  | Metrology | bitfield16 | R | 122378 | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 | 42380 | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 | 42381 | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 | 42382 | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 | 42392 | Element Angle |  | Metrology | float | R | 122391 | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | 42393 | [11 empty] | ALL
PULSE INPUTS | - | - | PULSE INPUTS | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 | 42401 | Pulse Input 1 Enable |  | Config | uint16 | R/W | 2400 | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 | 42402 | Pulse Input 1 Scale Factor |  | Config | float32 | R/W | 2401 | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 | 42403 |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 | 42404 | Pulse Input 1 Units |  | Config | string(4) | R/W | 2403 | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 | 42405 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 | 42406 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 | 42407 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 | 42408 | Pulse Input 1 Accumulator |  | Metrology | float32 | R | 2407 | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | 42409 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 | 42410 | Pulse Input 1 Accumulator Clear |  | User | unit16 | W | 2409 | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 | 42411 | Pulse Input 2 Enable |  | Config | uint16 | R/W | 2410 | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 | 42412 | Pulse Input 2 Scale Factor |  | Config | float32 | R/W | 2411 | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | 42413 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 | 42414 | Pulse Input 2 Units |  | Config | string(4) | R/W | 2413 | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 | 42415 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 | 42416 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 | 42417 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 | 42418 | Pulse Input 2 Accumulator |  | Metrology | float32 | R | 2417 | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | 42419 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 | 42420 | Pulse Input 2 Accumulator Clear |  | User | unit16 | W | 2419 | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 | 42421 | Pulse Input 3 Enable |  | Config | uint16 | R/W | 2420 | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 | 42422 | Pulse Input 3 Scale Factor |  | Config | float32 | R/W | 2421 | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | 42423 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 | 42424 | Pulse Input 3 Units |  | Config | string(4) | R/W | 2423 | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 | 42425 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 | 42426 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 | 42427 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 | 42428 | Pulse Input 3 Accumulator |  | Metrology | float32 | R | 2427 | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | 42429 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 | 42430 | Pulse Input 3 Accumulator Clear |  | User |  | W | 2429 | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 | 42431 | Pulse Input 4 Enable |  | Config | uint16 | R/W | 2430 | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 | 42432 | Pulse Input 4 Scale Factor |  | Config | float32 | R/W | 2431 | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | 42433 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 | 42434 | Pulse Input 4 Units |  | Config | string(4) | R/W | 2433 | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 | 42435 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 | 42436 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 | 42437 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 | 42438 | Pulse Input 4 Accumulator |  | Metrology | float32 | R | 2437 | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | 42439 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 | 42440 | Pulse Input 4 Accumulator Clear |  | User | unit16 | W | 2439 | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - | ALARMS | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 | 42452 | State of Alarm |  | Metrology | uint16 | R/W | 2451 | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 | 42453 | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 | 42454 | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 | 42455 | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 | 42456 | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 | 42457 | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 | 42458 | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 | 42459 | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W | 2458 | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 | 42460 | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W | 2459 | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Range Vin1 L1N Under | 2460 | 42461 | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W | 2460 | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 | 42462 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2N Under | 2462 | 42463 | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W | 2462 | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 | 42464 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3N Under | 2464 | 42465 | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W | 2464 | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 | 42466 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L1L2 Under | 2466 | 42467 | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W | 2466 | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 | 42468 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2L3 Under | 2468 | 42469 | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W | 2468 | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 | 42470 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3L1 Under | 2470 | 42471 | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W | 2470 | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 | 42472 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin2 L1N Under | 2472 | 42473 | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W | 2472 | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 | 42474 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2N Under | 2474 | 42475 | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W | 2474 | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 | 42476 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3N Under | 2476 | 42477 | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W | 2476 | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 | 42478 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L1L2 Under | 2478 | 42479 | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W | 2478 | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 | 42480 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2L3 Under | 2480 | 42481 | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W | 2480 | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 | 42482 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3L1 Under | 2482 | 42483 | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W | 2482 | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 | 42484 | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 | 42485 | Voltage Alarm Persistence | Sec | Config | uint16 | R/W | 2484 | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 | 42486 | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R | 2485 | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 | 42487 | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 | 42488 | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R | 2487 | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 | 42489 | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 | 42490 | Real Time Clock MSW |  | Config | uint16 | R/W | 2489 | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 | 42491 | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - | USER CONFIG POINTS 2 | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 | 42602 | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 | 42603 | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 | 42604 | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 | 42605 | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 | 42606 | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 | 42607 | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 | 42608 | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 | 42609 | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 | 42610 | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 | 42611 | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 | 42612 | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 | 42613 | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 | 42614 | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 | 42615 | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 | 42616 | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 | 42617 | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 | 42618 | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 | 42619 | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 | 42620 | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 | 42621 | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 | 42622 | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 | 42623 | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 | 42624 | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 | 42625 | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 | 42626 | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 | 42627 | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 | 42628 | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 | 42629 | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 | 42630 | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 | 42631 | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 | 42632 | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 | 42633 | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 | 42634 | BACnet Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | 2634 | 42635 | BACnet Description 1 | [8 empty] | 2 Char |  | ALL
BACnet Description 2 | 2635 | 42636 | BACnet Description 2 | [8 empty] | 2 Char |  | ALL
BACnet Description 3 | 2636 | 42637 | BACnet Description 3 | [8 empty] | 2 Char |  | ALL
BACnet Description 4 | 2637 | 42638 | BACnet Description 4 | [8 empty] | 2 Char |  | ALL
BACnet Description 5 | 2638 | 42639 | BACnet Description 5 | [8 empty] | 2 Char |  | ALL
BACnet Description 6 | 2639 | 42640 | BACnet Description 6 | [8 empty] | 2 Char |  | ALL
BACnet Description 7 | 2640 | 42641 | BACnet Description 7 | [8 empty] | 2 Char |  | ALL
BACnet Description 8 | 2641 | 42642 | BACnet Description 8 | [8 empty] | 2 Char |  | ALL
BACnet Description 9 | 2642 | 42643 | BACnet Description 9 | [8 empty] | 2 Char |  | ALL
BACnet Description 10 | 2643 | 42644 | BACnet Description 10 | [8 empty] | 2 Char |  | ALL
BACnet Description 11 | 2644 | 42645 | BACnet Description 11 | [8 empty] | 2 Char |  | ALL
BACnet Description 12 | 2645 | 42646 | BACnet Description 12 | [8 empty] | 2 Char |  | ALL
BACnet Description 13 | 2646 | 42647 | BACnet Description 13 | [8 empty] | 2 Char |  | ALL
BACnet Description 14 | 2647 | 42648 | BACnet Description 14 | [8 empty] | 2 Char |  | ALL
BACnet Description 15 | 2648 | 42649 | BACnet Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
VERIS EMULATION LEGACY REGISTERS | - | - | VERIS EMULATION LEGACY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Veris Emulation Mode | 2200 | 42201 | Set to Veris Emulation Mode |  | Config | uint16 | R/W |  |  |  | system | 0-1 | 1 = Report Slave ID as Veris Model H8036 | ALL
kWh System LSW | 0 | 40001 | kWh System LSW | kWh | Veris | uint32 | R |  |  |  | element |  |  | ALL
kWh System MSW | 1 | 40002 | kWh System MSW | kWh | Veris |  | R |  |  |  | element |  |  | ALL
kW System | 2 | 40003 | kW System | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVAR System | 3 | 40004 | kVAR System | kVAR | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVA System | 4 | 40005 | kVA System | kVA | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF System | 5 | 40006 | Apparent PF System | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts Line to Line Avg | 6 | 40007 | Volts Line to Line Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts Line to Neutral Avg | 7 | 40008 | Volts Line to Neutral Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps System Avg | 8 | 40009 | Amps System Avg | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L1 | 9 | 40010 | kW L1 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L2 | 10 | 40011 | kW L2 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L3 | 11 | 40012 | kW L3 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L1 | 12 | 40013 | Apparent PF L1 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L2 | 13 | 40014 | Apparent PF L2 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L3 | 14 | 40015 | Apparent PF L3 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts L1 to L2 | 15 | 40016 | Volts L1 to L2 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to L3 | 16 | 40017 | Volts L2 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to L3 | 17 | 40018 | Volts L1 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to Neutral | 18 | 40019 | Volts L1 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to Neutral | 19 | 40020 | Volts L2 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L3 to Neutral | 20 | 40021 | Volts L3 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps L1 | 21 | 40022 | Amps L1 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L2 | 22 | 40023 | Amps L2 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L3 | 23 | 40024 | Amps L3 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW System Avg | 24 | 40025 | kW System Avg | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Now | 25 | 40026 | kW Demand Sys Now (was Min) | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Max | 26 | 40027 | kW Demand Sys Max | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL

## N
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS --> | 14
BACNET OBJECT FLOOR --> | 130000
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 | 41002 | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | 41003 | [8 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 | 41004 | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 | 41005 | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 | 41006 | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | 41007 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | 41008 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | 41009 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | 41010 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | 41011 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | 41012 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | 41013 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | 41014 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | 41015 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | 41016 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | 41017 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | 41018 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | 41019 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | 41020 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | 41021 | [8 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 | 41022 | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | 41023 | [8 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | 41024 | [8 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | 41025 | [8 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | 41026 | [8 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | 41027 | [8 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | 41028 | [8 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | 41029 | [8 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | 41030 | [8 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | 41031 | [8 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | 41032 | [8 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | 41033 | [8 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | 41034 | [8 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | 41035 | [8 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | 41036 | [8 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | 41037 | [8 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 | 41038 | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | 41039 | [8 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | 41040 | [8 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | 41041 | [8 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | 41042 | [8 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | 41043 | [8 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | 41044 | [8 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | 41045 | [8 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 | 41046 | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | 41047 | [8 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | 41048 | [8 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | 41049 | [8 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | 41050 | [8 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | 41051 | [8 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | 41052 | [8 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | 41053 | [8 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 | 41054 | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | 41055 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | 41056 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | 41057 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | 41058 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | 41059 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | 41060 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | 41061 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | 41062 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | 41063 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | 41064 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | 41065 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | 41066 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | 41067 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | 41068 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | 41069 | [8 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 | 41070 | Modbus Device Address |  |  | unit16 | R/W | 1069 | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | 41071 | [8 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 | 41072 | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 | 41073 | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 | 41074 | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | 41075 | [8 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | 41076 | [8 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | 41077 | [8 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 | 41078 | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 | 41079 | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 | 41080 | IP Address |  |  | string(8) | R/W | 1079 | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | 41081 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | 41082 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | 41083 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | 41084 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | 41085 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | 41086 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | 41087 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 | 41088 | Netmask |  |  | string(8) | R/W | 1087 | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | 41089 | [8 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | 41090 | [8 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | 41091 | [8 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | 41092 | [8 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | 41093 | [8 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | 41094 | [8 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | 41095 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 | 41096 | Gateway |  |  | string(8) | R/W | 1095 | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | 41097 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | 41098 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | 41099 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | 41100 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | 41101 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | 41102 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | 41103 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 | 41104 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | 41105 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | 41106 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | 41107 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | 41108 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | 41109 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | 41110 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | 41111 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 | 41112 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | 41113 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | 41114 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | 41115 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | 41116 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | 41117 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | 41118 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | 41119 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 | 41120 | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | 41121 | [8 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | 41122 | [8 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | 41123 | [8 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 | 41124 | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | 41125 | [9 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 | 41126 | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 | 41127 | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 | 41128 | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | 41129 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | 41130 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | 41131 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 | 41132 | Interface baud rate in bits per second |  |  | uint32 | R/W | 1131 | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | 41133 | [8 empty] | system |  |  | ALL
SERIAL BITS | 1133 | 41134 | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 | 41135 | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 | 41136 | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 | 41137 | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 | 41138 | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 | 41139 | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 | 41140 | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 | 41141 | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 | 41142 | Current Avg Element | A | Metrology | float32 | R | 131141 | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | 41143 | [8 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 | 41144 | Current CH1 (A) | A | Metrology | float32 | R | 131143 | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | 41145 | [8 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 | 41146 | Current CH2 (B) | A | Metrology | float32 | R | 131145 | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | 41147 | [8 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 | 41148 | Current CH3 (C) | A | Metrology | float32 | R | 131147 | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | 41149 | [8 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 | 41150 | Voltage L to N Avg Element | V | Metrology | float32 | R | 131149 | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | 41151 | [8 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 | 41152 | Voltage L1 to N (AN) | V | Metrology | float32 | R | 131151 | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | 41153 | [8 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 | 41154 | Voltage L2 to N (BN) | V | Metrology | float32 | R | 131153 | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | 41155 | [8 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 | 41156 | Voltage L3 to N (CN) | V | Metrology | float32 | R | 131155 | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | 41157 | [8 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 | 41158 | Voltage L to L Avg Element | V | Metrology | float32 | R | 131157 | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | 41159 | [8 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 | 41160 | Voltage L1 to L2 (AB) | V | Metrology | float32 | R | 131159 | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | 41161 | [8 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 | 41162 | Voltage L2 to L3 (BC) | V | Metrology | float32 | R | 131161 | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | 41163 | [8 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 | 41164 | Voltage L3 to L1 (CA) | V | Metrology | float32 | R | 131163 | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | 41165 | [8 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 | 41166 | Line Frequency | Hz | Metrology | float32 | R | 131165 | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | 41167 | [8 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 | 41168 | Power Sum Element | kW | Metrology | float32 | R | 131167 | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | 41169 | [8 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 | 41170 | Power CH1 (A) | kW | Metrology | float32 | R | 131169 | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | 41171 | [8 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 | 41172 | Power CH2 (B) | kW | Metrology | float32 | R | 131171 | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | 41173 | [8 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 | 41174 | Power CH3 (C) | kW | Metrology | float32 | R | 131173 | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | 41175 | [8 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 | 41176 | VA Sum Element | kVA | Metrology | float32 | R | 131175 | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | 41177 | [8 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 | 41178 | VA CH1 (A) | kVA | Metrology | float32 | R | 131177 | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | 41179 | [8 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 | 41180 | VA CH2 (B) | kVA | Metrology | float32 | R | 131179 | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | 41181 | [8 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 | 41182 | VA CH3 (C) | kVA | Metrology | float32 | R | 131181 | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | 41183 | [8 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 | 41184 | VAR Sum Element | kVAr | Metrology | float32 | R | 131183 | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | 41185 | [8 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 | 41186 | VAR CH1 (A) | kVAr | Metrology | float32 | R | 131185 | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | 41187 | [8 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 | 41188 | VAR CH2 (B) | kVAr | Metrology | float32 | R | 131187 | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | 41189 | [8 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 | 41190 | VAR CH3 (C) | kVAr | Metrology | float32 | R | 131189 | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | 41191 | [8 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 | 41192 | Apparent PF Avg Element | PF | Metrology | float32 | R | 131191 | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | 41193 | [8 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 | 41194 | Apparent PF CH1 (A) | PF | Metrology | float32 | R | 131193 | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | 41195 | [8 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 | 41196 | Apparent PF CH2 (B) | PF | Metrology | float32 | R | 131195 | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | 41197 | [8 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 | 41198 | Apparent PF CH3 ( C) | PF | Metrology | float32 | R | 131197 | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | 41199 | [8 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 | 41200 | Exported Energy Sum Element | kWh | Metrology | float32 | R | 131199 | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | 41201 | [8 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 | 41202 | Exported Energy CH1 (A) | kWh | Metrology | float32 | R | 131201 | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | 41203 | [8 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 | 41204 | Exported Energy CH2 (B) | kWh | Metrology | float32 | R | 131203 | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | 41205 | [8 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 | 41206 | Exported Energy CH3 (C) | kWh | Metrology | float32 | R | 131205 | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | 41207 | [8 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 | 41208 | Imported Energy Sum Element | kWh | Metrology | float32 | R | 131207 | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | 41209 | [8 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 | 41210 | Imported Energy CH1 (A) | kWh | Metrology | float32 | R | 131209 | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | 41211 | [8 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 | 41212 | Imported Energy CH2 (B) | kWh | Metrology | float32 | R | 131211 | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | 41213 | [8 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 | 41214 | Imported Energy CH3 (C) | kWh | Metrology | float32 | R | 131213 | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | 41215 | [8 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 | 41216 | Exported VAh Sum Element | kVAh | Metrology | float32 | R | 131215 | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | 41217 | [8 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 | 41218 | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R | 131217 | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | 41219 | [8 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 | 41220 | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R | 131219 | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | 41221 | [8 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 | 41222 | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R | 131221 | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | 41223 | [8 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 | 41224 | Imported VAh Sum Element | kVAh | Metrology | float32 | R | 131223 | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | 41225 | [8 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 | 41226 | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R | 131225 | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | 41227 | [8 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 | 41228 | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R | 131227 | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | 41229 | [8 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 | 41230 | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R | 131229 | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | 41231 | [8 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 | 41232 | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R | 131231 | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | 41233 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 | 41234 | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R | 131233 | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | 41235 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 | 41236 | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R | 131235 | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | 41237 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 | 41238 | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R | 131237 | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | 41239 | [8 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 | 41240 | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R | 131239 | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | 41241 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 | 41242 | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R | 131241 | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | 41243 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 | 41244 | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R | 131243 | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | 41245 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 | 41246 | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R | 131245 | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | 41247 | [8 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 | 41248 | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R | 131247 | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | 41249 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 | 41250 | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R | 131249 | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | 41251 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 | 41252 | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R | 131251 | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | 41253 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 | 41254 | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R | 131253 | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | 41255 | [8 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 | 41256 | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R | 131255 | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | 41257 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 | 41258 | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R | 131257 | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | 41259 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 | 41260 | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R | 131259 | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | 41261 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 | 41262 | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R | 131261 | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | 41263 | [8 empty] | element |  |  | ALL
Events MSW | 1263 | 41264 | Events MSW |  |  | bitfield32 | R | 1263 | AI | Events | system |  |  | ALL
Events LSW | 1264 | 41265 | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 | 41266 | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 | 41267 | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
FACTORY REGISTERS | - | - | FACTORY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Factory Unlock Register | 2000 | 42001 | Factory Unlock Register |  | Factory | unit16 | R/W |  |  |  | system |  | Reserved | ALL
Factory Reset | 2001 | 42002 | Factory Reset |  | Factory | unit16 | R/W |  |  |  | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
OEM Vendor ID | 2002 | 42003 | OEM Vendor ID |  | Factory | unit16 | R |  |  |  | system |  | Reserved | ALL
FACTORY_CONFIG | 2003 | 42004 | Factory Config |  | Factory | unit16 | R |  |  |  | system | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable | ALL
USER COMMAND POINTS | - | - | USER COMMAND POINTS | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 | 42101 | Reset (software) processor |  | User | unit16 | W | 2100 | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 | 42102 | Clear all accumulated measurements (CAM) |  | User | unit16 | W | 2101 | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 | 42103 | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W | 132102 | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 | 42104 | Clear Peak Demand Element |  | User | unit16 | W | 132103 | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 | 42105 | Clear Peak Demand All |  | User | unit16 | W | 2104 | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 | 42106 | Reset to User Defaults |  | User | unit16 | W | 2105 | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - | USER CONFIG POINTS | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 | 42202 | Sliding or Fixed |  | Config | enum16 | R | 2201 | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 | 42203 | Demand Window | Min | Config | uint16 | R | 2202 | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 | 42204 | Volt Multiplier VINPUT1 |  | Config | float32 | R/W | 2203 | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | 42205 | [8 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 | 42206 | Volt Multiplier VINPUT2 |  | Config | float32 | R/W | 2205 | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | 42207 | [8 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 | 42208 | Service Type |  | Config | enum16 | R/W | 132207 | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 | 42209 | Snap MV Threshold | PER | Config | float32 | R/W | 2208 | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | 42210 | [8 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 | 42211 | Snap Rog Threshold | PER | Config | float32 | R/W | 2210 | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | 42212 | [8 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 | 42213 | Snap Volt Threshold | V | Config | float32 | R/W | 2212 | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | 42214 | [8 empty] | system |  |  | ALL
Communications Mode | 2214 | 42215 | Communications Mode |  | Config |  |  | 2214 | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 | 42216 | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W | 2215 | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | 42217 | [8 empty] | system |  |  | ALL
Voltage Input Element | 2217 | 42218 | Element Voltage Input |  | Config | enum16 | R/W | 132217 | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 | 42219 | CT1 RANGE | A | Config | float32 | R/W | 132218 | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | 42220 | [8 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 | 42221 | Voltage Reference for CT1 |  | Config | enum16 | R/W | 132220 | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 | 42222 | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W | 132221 | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | 42223 | [8 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 | 42224 | CT1 TYPE |  | Config | enum16 | R/W | 132223 | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 | 42225 | CT1 PHASE SHIFT | Deg | Config | float32 | R/W | 132224 | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | 42226 | [8 empty] | element |  |  | ALL
CH1 CT Sign | 2226 | 42227 | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W | 132226 | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 | 42228 | CT2 RANGE | A | Config | float32 | R/W | 132227 | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | 42229 | [8 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 | 42230 | Voltage Reference for CT2 |  | Config | enum16 | R/W | 132229 | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 | 42231 | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W | 132230 | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | 42232 | [8 empty] | element | >0 |  | ALL
CH2 CT type | 2232 | 42233 | CT2 TYPE |  | Config | enum16 | R/W | 132232 | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 | 42234 | CT2 PHASE SHIFT | Deg | Config | float32 | R/W | 132233 | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | 42235 | [8 empty] | element |  |  | ALL
CH2 CT Sign | 2235 | 42236 | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W | 132235 | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 | 42237 | CT3 INTEGER | A | Config | float32 | R/W | 132236 | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | 42238 | [8 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 | 42239 | Voltage Reference for CT3 |  | Config | enum16 | R/W | 132238 | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 | 42240 | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W | 132239 | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | 42241 | [8 empty] | element | >0 |  | ALL
CH3 CT type | 2241 | 42242 | CT3 TYPE |  | Config | enum16 | R/W | 132241 | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 | 42243 | CT3 PHASE SHIFT | Deg | Config | float32 | R/W | 132242 | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | 42244 | [8 empty] | element |  |  | ALL
CH3 CT Sign | 2244 | 42245 | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W | 132244 | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 | 42246 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 | 42247 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 | 42248 | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 | 42249 | PF Sign Convention |  | Config | uint16 | R/W | 2248 | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 | 42250 | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 | 42251 | BACnet UDP Port |  | Config | uint16 | R/W | 2250 | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 | 42252 | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 | 42253 | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | 42254 | [8 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 | 42261 | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | 42262 | [11 empty] | ALL
BACnet Max Info Frames | 2262 | 42263 | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 | 42264 | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 | 42265 | BBMD IP Address |  | Config | string(16) | R/W | 2264 | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | 42266 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | 42267 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | 42268 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | 42269 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | 42270 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | 42271 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | 42272 | [9 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 | 42273 | LCD/WebApp Read Password |  | Config | uint16 | R/W | 2272 | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 | 42274 | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 | 42275 | Customer Line frequency |  | Config | float | R/W | 2274 | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | 42276 | [10 empty] | Reserved | ALL
Communications Interface Configured | 2276 | 42277 | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 | 42278 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 | 42279 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 | 42280 | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 | 42281 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 | 42282 | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 | 42283 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 | 42284 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 | 42285 | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 | 42286 | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 | 42287 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 | 42288 | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 | 42289 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 | 42290 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 | 42291 | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 | 42292 | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | 42293 | [11 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 | 42294 | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | 42295 | [11 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 | 42296 | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 | 42297 | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - | METROLOGY POINTS | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 | 42301 | Displacement PF Avg Element | dPF | Metrology | float32 | R | 132300 | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | 42302 | [11 empty] | ALL
Displacement PF CH1 (MSW) | 2302 | 42303 | Displacement PF CH1 (A) | dPF | Metrology | float32 | R | 132302 | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | 42304 | [11 empty] | ALL
Displacement PF CH2 (MSW) | 2304 | 42305 | Displacement PF CH2 (B) | dPF | Metrology | float32 | R | 132304 | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | 42306 | [11 empty] | ALL
Displacement PF CH3 (MSW) | 2306 | 42307 | Displacement PF CH3 (C) | dPF | Metrology | float32 | R | 132306 | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | 42308 | [11 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 | 42309 | Avg Apparent PF Element | aPF | Metrology | float32 | R | 132308 | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | 42310 | [11 empty] | ALL
Apparent PF CH1 (MSW) | 2310 | 42311 | Apparent PF CH1 (A) | aPF | Metrology | float32 | R | 132310 | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | 42312 | [11 empty] | ALL
Apparent PF CH2 (MSW) | 2312 | 42313 | Apparent PF CH2 (B) | aPF | Metrology | float32 | R | 132312 | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | 42314 | [11 empty] | ALL
Apparent PF CH3 (MSW) | 2314 | 42315 | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R | 132314 | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | 42316 | [11 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 | 42317 | Distortion PF Avg Element | tPF | Metrology | float32 | R | 132316 | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | 42318 | [11 empty] | ALL
Distortion PF CH1 (MSW) | 2318 | 42319 | Distortion PF CH1 (A) | tPF | Metrology | float32 | R | 132318 | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | 42320 | [11 empty] | ALL
Distortion PF CH2 (MSW) | 2320 | 42321 | Distortion PF CH2 (B) | tPF | Metrology | float32 | R | 132320 | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | 42322 | [11 empty] | ALL
Distortion PF CH3 (MSW) | 2322 | 42323 | Distortion PF CH3 (C) | tPF | Metrology | float32 | R | 132322 | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | 42324 | [11 empty] | ALL
THD Avg Element (MSW) | 2324 | 42325 | THD Avg Element | % | Metrology | float32 | R | 132324 | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | 42326 | [11 empty] | ALL
THD CH1 (MSW) | 2326 | 42327 | THD CH1 (A) | % | Metrology | float32 | R | 132326 | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | 42328 | [11 empty] | ALL
THD CH2 (MSW) | 2328 | 42329 | THD CH2 (B) | % | Metrology | float32 | R | 132328 | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | 42330 | [11 empty] | ALL
THD CH3 (MSW) | 2330 | 42331 | THD CH3 (C) | % | Metrology | float32 | R | 132330 | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | 42332 | [11 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 | 42333 | Power Demand Max Interval Element | kW | Metrology | float32 | R | 132332 | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | 42334 | [11 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 | 42335 | Power Demand This Interval Element | kW | Metrology | float32 | R | 132334 | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | 42336 | [11 empty] | ALL
VA Peak Demand Element (MSW) | 2336 | 42337 | VA Demand Max Interval Element | kVA | Metrology | float32 | R | 132336 | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | 42338 | [11 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 | 42339 | VA Demand This Interval Element | kVA | Metrology | float32 | R | 132338 | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | 42340 | [11 empty] | ALL
Not Used | 2340 | 42341 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 | 42342 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 | 42343 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 | 42344 | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 | 42345 | Energy Net Sum Element | kWh | Metrology | float32 | R | 132344 | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | 42346 | [8 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 | 42347 | Energy Net CH1 | kWh | Metrology | float32 | R | 132346 | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | 42348 | [8 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 | 42349 | Energy Net CH2 | kWh | Metrology | float32 | R | 132348 | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | 42350 | [8 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 | 42351 | Energy Net CH3 | kWh | Metrology | float32 | R | 132350 | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | 42352 | [8 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 | 42353 | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R | 132352 | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | 42354 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 | 42355 | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R | 132354 | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | 42356 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 | 42357 | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R | 132356 | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | 42358 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 | 42359 | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R | 132358 | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | 42360 | [8 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 | 42361 | VARh Net Sum Element | kVArh | Metrology | float32 | R | 132360 | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | 42362 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 | 42363 | VARh Net CH1 | kVArh | Metrology | float32 | R | 132362 | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | 42364 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 | 42365 | VARh Net CH2 | kVArh | Metrology | float32 | R | 132364 | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | 42366 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 | 42367 | VARh Net CH3 | kVArh | Metrology | float32 | R | 132366 | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | 42368 | [8 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 | 42369 | Time Since Reset MSW | Sec | Metrology | uint32 |  | 2368 | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 | 42370 | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 | 42371 | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 | 42372 | CH1 Angle | Deg | Metrology | float32 | R | 132371 | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | 42373 | [8 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 | 42374 | CH2 Angle | Deg | Metrology | float32 | R | 132373 | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | 42375 | [8 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 | 42376 | CH3 Angle | Deg | Metrology | float32 | R | 132375 | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | 42377 | [11 empty] | ALL
Phase Chek System Status | 2377 | 42378 | System Phase Check Status |  | Metrology | bitfield16 | R | 2377 | BV | Phase Check System Status | system | 0,1 | 0 (All Channels OK), 1(Somewhere a channel is reading a dPF < 0.55), check register 2378 for each Element | ALL
Phase Chek Element Status | 2378 | 42379 | Element Phase Check Status |  | Metrology | bitfield16 | R | 132378 | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 | 42380 | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 | 42381 | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 | 42382 | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 | 42392 | Element Angle |  | Metrology | float | R | 132391 | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | 42393 | [11 empty] | ALL
PULSE INPUTS | - | - | PULSE INPUTS | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 | 42401 | Pulse Input 1 Enable |  | Config | uint16 | R/W | 2400 | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 | 42402 | Pulse Input 1 Scale Factor |  | Config | float32 | R/W | 2401 | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 | 42403 |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 | 42404 | Pulse Input 1 Units |  | Config | string(4) | R/W | 2403 | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 | 42405 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 | 42406 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 | 42407 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 | 42408 | Pulse Input 1 Accumulator |  | Metrology | float32 | R | 2407 | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | 42409 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 | 42410 | Pulse Input 1 Accumulator Clear |  | User | unit16 | W | 2409 | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 | 42411 | Pulse Input 2 Enable |  | Config | uint16 | R/W | 2410 | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 | 42412 | Pulse Input 2 Scale Factor |  | Config | float32 | R/W | 2411 | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | 42413 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 | 42414 | Pulse Input 2 Units |  | Config | string(4) | R/W | 2413 | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 | 42415 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 | 42416 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 | 42417 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 | 42418 | Pulse Input 2 Accumulator |  | Metrology | float32 | R | 2417 | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | 42419 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 | 42420 | Pulse Input 2 Accumulator Clear |  | User | unit16 | W | 2419 | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 | 42421 | Pulse Input 3 Enable |  | Config | uint16 | R/W | 2420 | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 | 42422 | Pulse Input 3 Scale Factor |  | Config | float32 | R/W | 2421 | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | 42423 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 | 42424 | Pulse Input 3 Units |  | Config | string(4) | R/W | 2423 | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 | 42425 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 | 42426 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 | 42427 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 | 42428 | Pulse Input 3 Accumulator |  | Metrology | float32 | R | 2427 | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | 42429 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 | 42430 | Pulse Input 3 Accumulator Clear |  | User |  | W | 2429 | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 | 42431 | Pulse Input 4 Enable |  | Config | uint16 | R/W | 2430 | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 | 42432 | Pulse Input 4 Scale Factor |  | Config | float32 | R/W | 2431 | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | 42433 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 | 42434 | Pulse Input 4 Units |  | Config | string(4) | R/W | 2433 | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 | 42435 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 | 42436 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 | 42437 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 | 42438 | Pulse Input 4 Accumulator |  | Metrology | float32 | R | 2437 | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | 42439 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 | 42440 | Pulse Input 4 Accumulator Clear |  | User | unit16 | W | 2439 | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - | ALARMS | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 | 42452 | State of Alarm |  | Metrology | uint16 | R/W | 2451 | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 | 42453 | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 | 42454 | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 | 42455 | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 | 42456 | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 | 42457 | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 | 42458 | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 | 42459 | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W | 2458 | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 | 42460 | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W | 2459 | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Range Vin1 L1N Under | 2460 | 42461 | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W | 2460 | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 | 42462 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2N Under | 2462 | 42463 | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W | 2462 | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 | 42464 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3N Under | 2464 | 42465 | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W | 2464 | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 | 42466 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L1L2 Under | 2466 | 42467 | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W | 2466 | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 | 42468 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2L3 Under | 2468 | 42469 | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W | 2468 | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 | 42470 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3L1 Under | 2470 | 42471 | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W | 2470 | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 | 42472 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin2 L1N Under | 2472 | 42473 | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W | 2472 | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 | 42474 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2N Under | 2474 | 42475 | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W | 2474 | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 | 42476 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3N Under | 2476 | 42477 | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W | 2476 | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 | 42478 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L1L2 Under | 2478 | 42479 | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W | 2478 | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 | 42480 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2L3 Under | 2480 | 42481 | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W | 2480 | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 | 42482 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3L1 Under | 2482 | 42483 | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W | 2482 | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 | 42484 | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 | 42485 | Voltage Alarm Persistence | Sec | Config | uint16 | R/W | 2484 | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 | 42486 | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R | 2485 | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 | 42487 | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 | 42488 | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R | 2487 | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 | 42489 | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 | 42490 | Real Time Clock MSW |  | Config | uint16 | R/W | 2489 | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 | 42491 | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - | USER CONFIG POINTS 2 | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 | 42602 | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 | 42603 | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 | 42604 | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 | 42605 | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 | 42606 | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 | 42607 | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 | 42608 | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 | 42609 | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 | 42610 | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 | 42611 | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 | 42612 | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 | 42613 | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 | 42614 | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 | 42615 | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 | 42616 | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 | 42617 | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 | 42618 | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 | 42619 | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 | 42620 | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 | 42621 | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 | 42622 | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 | 42623 | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 | 42624 | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 | 42625 | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 | 42626 | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 | 42627 | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 | 42628 | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 | 42629 | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 | 42630 | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 | 42631 | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 | 42632 | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 | 42633 | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 | 42634 | BACnet Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | 2634 | 42635 | BACnet Description 1 | [8 empty] | 2 Char |  | ALL
BACnet Description 2 | 2635 | 42636 | BACnet Description 2 | [8 empty] | 2 Char |  | ALL
BACnet Description 3 | 2636 | 42637 | BACnet Description 3 | [8 empty] | 2 Char |  | ALL
BACnet Description 4 | 2637 | 42638 | BACnet Description 4 | [8 empty] | 2 Char |  | ALL
BACnet Description 5 | 2638 | 42639 | BACnet Description 5 | [8 empty] | 2 Char |  | ALL
BACnet Description 6 | 2639 | 42640 | BACnet Description 6 | [8 empty] | 2 Char |  | ALL
BACnet Description 7 | 2640 | 42641 | BACnet Description 7 | [8 empty] | 2 Char |  | ALL
BACnet Description 8 | 2641 | 42642 | BACnet Description 8 | [8 empty] | 2 Char |  | ALL
BACnet Description 9 | 2642 | 42643 | BACnet Description 9 | [8 empty] | 2 Char |  | ALL
BACnet Description 10 | 2643 | 42644 | BACnet Description 10 | [8 empty] | 2 Char |  | ALL
BACnet Description 11 | 2644 | 42645 | BACnet Description 11 | [8 empty] | 2 Char |  | ALL
BACnet Description 12 | 2645 | 42646 | BACnet Description 12 | [8 empty] | 2 Char |  | ALL
BACnet Description 13 | 2646 | 42647 | BACnet Description 13 | [8 empty] | 2 Char |  | ALL
BACnet Description 14 | 2647 | 42648 | BACnet Description 14 | [8 empty] | 2 Char |  | ALL
BACnet Description 15 | 2648 | 42649 | BACnet Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
VERIS EMULATION LEGACY REGISTERS | - | - | VERIS EMULATION LEGACY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Veris Emulation Mode | 2200 | 42201 | Set to Veris Emulation Mode |  | Config | uint16 | R/W |  |  |  | system | 0-1 | 1 = Report Slave ID as Veris Model H8036 | ALL
kWh System LSW | 0 | 40001 | kWh System LSW | kWh | Veris | uint32 | R |  |  |  | element |  |  | ALL
kWh System MSW | 1 | 40002 | kWh System MSW | kWh | Veris |  | R |  |  |  | element |  |  | ALL
kW System | 2 | 40003 | kW System | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVAR System | 3 | 40004 | kVAR System | kVAR | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVA System | 4 | 40005 | kVA System | kVA | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF System | 5 | 40006 | Apparent PF System | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts Line to Line Avg | 6 | 40007 | Volts Line to Line Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts Line to Neutral Avg | 7 | 40008 | Volts Line to Neutral Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps System Avg | 8 | 40009 | Amps System Avg | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L1 | 9 | 40010 | kW L1 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L2 | 10 | 40011 | kW L2 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L3 | 11 | 40012 | kW L3 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L1 | 12 | 40013 | Apparent PF L1 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L2 | 13 | 40014 | Apparent PF L2 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L3 | 14 | 40015 | Apparent PF L3 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts L1 to L2 | 15 | 40016 | Volts L1 to L2 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to L3 | 16 | 40017 | Volts L2 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to L3 | 17 | 40018 | Volts L1 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to Neutral | 18 | 40019 | Volts L1 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to Neutral | 19 | 40020 | Volts L2 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L3 to Neutral | 20 | 40021 | Volts L3 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps L1 | 21 | 40022 | Amps L1 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L2 | 22 | 40023 | Amps L2 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L3 | 23 | 40024 | Amps L3 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW System Avg | 24 | 40025 | kW System Avg | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Now | 25 | 40026 | kW Demand Sys Now (was Min) | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Max | 26 | 40027 | kW Demand Sys Max | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL

## O
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS --> | 15
BACNET OBJECT FLOOR --> | 140000
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 | 41002 | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | 41003 | [8 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 | 41004 | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 | 41005 | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 | 41006 | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | 41007 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | 41008 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | 41009 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | 41010 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | 41011 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | 41012 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | 41013 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | 41014 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | 41015 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | 41016 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | 41017 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | 41018 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | 41019 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | 41020 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | 41021 | [8 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 | 41022 | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | 41023 | [8 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | 41024 | [8 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | 41025 | [8 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | 41026 | [8 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | 41027 | [8 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | 41028 | [8 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | 41029 | [8 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | 41030 | [8 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | 41031 | [8 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | 41032 | [8 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | 41033 | [8 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | 41034 | [8 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | 41035 | [8 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | 41036 | [8 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | 41037 | [8 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 | 41038 | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | 41039 | [8 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | 41040 | [8 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | 41041 | [8 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | 41042 | [8 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | 41043 | [8 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | 41044 | [8 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | 41045 | [8 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 | 41046 | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | 41047 | [8 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | 41048 | [8 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | 41049 | [8 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | 41050 | [8 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | 41051 | [8 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | 41052 | [8 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | 41053 | [8 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 | 41054 | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | 41055 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | 41056 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | 41057 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | 41058 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | 41059 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | 41060 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | 41061 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | 41062 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | 41063 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | 41064 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | 41065 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | 41066 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | 41067 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | 41068 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | 41069 | [8 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 | 41070 | Modbus Device Address |  |  | unit16 | R/W | 1069 | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | 41071 | [8 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 | 41072 | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 | 41073 | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 | 41074 | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | 41075 | [8 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | 41076 | [8 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | 41077 | [8 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 | 41078 | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 | 41079 | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 | 41080 | IP Address |  |  | string(8) | R/W | 1079 | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | 41081 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | 41082 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | 41083 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | 41084 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | 41085 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | 41086 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | 41087 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 | 41088 | Netmask |  |  | string(8) | R/W | 1087 | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | 41089 | [8 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | 41090 | [8 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | 41091 | [8 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | 41092 | [8 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | 41093 | [8 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | 41094 | [8 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | 41095 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 | 41096 | Gateway |  |  | string(8) | R/W | 1095 | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | 41097 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | 41098 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | 41099 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | 41100 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | 41101 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | 41102 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | 41103 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 | 41104 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | 41105 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | 41106 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | 41107 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | 41108 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | 41109 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | 41110 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | 41111 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 | 41112 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | 41113 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | 41114 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | 41115 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | 41116 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | 41117 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | 41118 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | 41119 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 | 41120 | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | 41121 | [8 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | 41122 | [8 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | 41123 | [8 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 | 41124 | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | 41125 | [9 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 | 41126 | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 | 41127 | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 | 41128 | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | 41129 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | 41130 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | 41131 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 | 41132 | Interface baud rate in bits per second |  |  | uint32 | R/W | 1131 | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | 41133 | [8 empty] | system |  |  | ALL
SERIAL BITS | 1133 | 41134 | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 | 41135 | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 | 41136 | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 | 41137 | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 | 41138 | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 | 41139 | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 | 41140 | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 | 41141 | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 | 41142 | Current Avg Element | A | Metrology | float32 | R | 141141 | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | 41143 | [8 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 | 41144 | Current CH1 (A) | A | Metrology | float32 | R | 141143 | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | 41145 | [8 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 | 41146 | Current CH2 (B) | A | Metrology | float32 | R | 141145 | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | 41147 | [8 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 | 41148 | Current CH3 (C) | A | Metrology | float32 | R | 141147 | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | 41149 | [8 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 | 41150 | Voltage L to N Avg Element | V | Metrology | float32 | R | 141149 | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | 41151 | [8 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 | 41152 | Voltage L1 to N (AN) | V | Metrology | float32 | R | 141151 | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | 41153 | [8 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 | 41154 | Voltage L2 to N (BN) | V | Metrology | float32 | R | 141153 | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | 41155 | [8 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 | 41156 | Voltage L3 to N (CN) | V | Metrology | float32 | R | 141155 | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | 41157 | [8 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 | 41158 | Voltage L to L Avg Element | V | Metrology | float32 | R | 141157 | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | 41159 | [8 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 | 41160 | Voltage L1 to L2 (AB) | V | Metrology | float32 | R | 141159 | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | 41161 | [8 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 | 41162 | Voltage L2 to L3 (BC) | V | Metrology | float32 | R | 141161 | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | 41163 | [8 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 | 41164 | Voltage L3 to L1 (CA) | V | Metrology | float32 | R | 141163 | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | 41165 | [8 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 | 41166 | Line Frequency | Hz | Metrology | float32 | R | 141165 | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | 41167 | [8 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 | 41168 | Power Sum Element | kW | Metrology | float32 | R | 141167 | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | 41169 | [8 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 | 41170 | Power CH1 (A) | kW | Metrology | float32 | R | 141169 | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | 41171 | [8 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 | 41172 | Power CH2 (B) | kW | Metrology | float32 | R | 141171 | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | 41173 | [8 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 | 41174 | Power CH3 (C) | kW | Metrology | float32 | R | 141173 | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | 41175 | [8 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 | 41176 | VA Sum Element | kVA | Metrology | float32 | R | 141175 | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | 41177 | [8 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 | 41178 | VA CH1 (A) | kVA | Metrology | float32 | R | 141177 | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | 41179 | [8 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 | 41180 | VA CH2 (B) | kVA | Metrology | float32 | R | 141179 | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | 41181 | [8 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 | 41182 | VA CH3 (C) | kVA | Metrology | float32 | R | 141181 | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | 41183 | [8 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 | 41184 | VAR Sum Element | kVAr | Metrology | float32 | R | 141183 | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | 41185 | [8 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 | 41186 | VAR CH1 (A) | kVAr | Metrology | float32 | R | 141185 | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | 41187 | [8 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 | 41188 | VAR CH2 (B) | kVAr | Metrology | float32 | R | 141187 | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | 41189 | [8 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 | 41190 | VAR CH3 (C) | kVAr | Metrology | float32 | R | 141189 | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | 41191 | [8 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 | 41192 | Apparent PF Avg Element | PF | Metrology | float32 | R | 141191 | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | 41193 | [8 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 | 41194 | Apparent PF CH1 (A) | PF | Metrology | float32 | R | 141193 | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | 41195 | [8 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 | 41196 | Apparent PF CH2 (B) | PF | Metrology | float32 | R | 141195 | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | 41197 | [8 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 | 41198 | Apparent PF CH3 ( C) | PF | Metrology | float32 | R | 141197 | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | 41199 | [8 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 | 41200 | Exported Energy Sum Element | kWh | Metrology | float32 | R | 141199 | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | 41201 | [8 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 | 41202 | Exported Energy CH1 (A) | kWh | Metrology | float32 | R | 141201 | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | 41203 | [8 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 | 41204 | Exported Energy CH2 (B) | kWh | Metrology | float32 | R | 141203 | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | 41205 | [8 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 | 41206 | Exported Energy CH3 (C) | kWh | Metrology | float32 | R | 141205 | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | 41207 | [8 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 | 41208 | Imported Energy Sum Element | kWh | Metrology | float32 | R | 141207 | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | 41209 | [8 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 | 41210 | Imported Energy CH1 (A) | kWh | Metrology | float32 | R | 141209 | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | 41211 | [8 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 | 41212 | Imported Energy CH2 (B) | kWh | Metrology | float32 | R | 141211 | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | 41213 | [8 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 | 41214 | Imported Energy CH3 (C) | kWh | Metrology | float32 | R | 141213 | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | 41215 | [8 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 | 41216 | Exported VAh Sum Element | kVAh | Metrology | float32 | R | 141215 | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | 41217 | [8 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 | 41218 | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R | 141217 | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | 41219 | [8 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 | 41220 | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R | 141219 | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | 41221 | [8 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 | 41222 | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R | 141221 | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | 41223 | [8 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 | 41224 | Imported VAh Sum Element | kVAh | Metrology | float32 | R | 141223 | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | 41225 | [8 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 | 41226 | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R | 141225 | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | 41227 | [8 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 | 41228 | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R | 141227 | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | 41229 | [8 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 | 41230 | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R | 141229 | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | 41231 | [8 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 | 41232 | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R | 141231 | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | 41233 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 | 41234 | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R | 141233 | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | 41235 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 | 41236 | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R | 141235 | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | 41237 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 | 41238 | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R | 141237 | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | 41239 | [8 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 | 41240 | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R | 141239 | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | 41241 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 | 41242 | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R | 141241 | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | 41243 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 | 41244 | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R | 141243 | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | 41245 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 | 41246 | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R | 141245 | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | 41247 | [8 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 | 41248 | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R | 141247 | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | 41249 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 | 41250 | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R | 141249 | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | 41251 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 | 41252 | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R | 141251 | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | 41253 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 | 41254 | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R | 141253 | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | 41255 | [8 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 | 41256 | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R | 141255 | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | 41257 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 | 41258 | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R | 141257 | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | 41259 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 | 41260 | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R | 141259 | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | 41261 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 | 41262 | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R | 141261 | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | 41263 | [8 empty] | element |  |  | ALL
Events MSW | 1263 | 41264 | Events MSW |  |  | bitfield32 | R | 1263 | AI | Events | system |  |  | ALL
Events LSW | 1264 | 41265 | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 | 41266 | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 | 41267 | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
FACTORY REGISTERS | - | - | FACTORY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Factory Unlock Register | 2000 | 42001 | Factory Unlock Register |  | Factory | unit16 | R/W |  |  |  | system |  | Reserved | ALL
Factory Reset | 2001 | 42002 | Factory Reset |  | Factory | unit16 | R/W |  |  |  | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
OEM Vendor ID | 2002 | 42003 | OEM Vendor ID |  | Factory | unit16 | R |  |  |  | system |  | Reserved | ALL
FACTORY_CONFIG | 2003 | 42004 | Factory Config |  | Factory | unit16 | R |  |  |  | system | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable | ALL
USER COMMAND POINTS | - | - | USER COMMAND POINTS | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 | 42101 | Reset (software) processor |  | User | unit16 | W | 2100 | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 | 42102 | Clear all accumulated measurements (CAM) |  | User | unit16 | W | 2101 | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 | 42103 | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W | 142102 | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 | 42104 | Clear Peak Demand Element |  | User | unit16 | W | 142103 | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 | 42105 | Clear Peak Demand All |  | User | unit16 | W | 2104 | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 | 42106 | Reset to User Defaults |  | User | unit16 | W | 2105 | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - | USER CONFIG POINTS | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 | 42202 | Sliding or Fixed |  | Config | enum16 | R | 2201 | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 | 42203 | Demand Window | Min | Config | uint16 | R | 2202 | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 | 42204 | Volt Multiplier VINPUT1 |  | Config | float32 | R/W | 2203 | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | 42205 | [8 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 | 42206 | Volt Multiplier VINPUT2 |  | Config | float32 | R/W | 2205 | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | 42207 | [8 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 | 42208 | Service Type |  | Config | enum16 | R/W | 142207 | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 | 42209 | Snap MV Threshold | PER | Config | float32 | R/W | 2208 | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | 42210 | [8 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 | 42211 | Snap Rog Threshold | PER | Config | float32 | R/W | 2210 | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | 42212 | [8 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 | 42213 | Snap Volt Threshold | V | Config | float32 | R/W | 2212 | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | 42214 | [8 empty] | system |  |  | ALL
Communications Mode | 2214 | 42215 | Communications Mode |  | Config |  |  | 2214 | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 | 42216 | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W | 2215 | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | 42217 | [8 empty] | system |  |  | ALL
Voltage Input Element | 2217 | 42218 | Element Voltage Input |  | Config | enum16 | R/W | 142217 | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 | 42219 | CT1 RANGE | A | Config | float32 | R/W | 142218 | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | 42220 | [8 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 | 42221 | Voltage Reference for CT1 |  | Config | enum16 | R/W | 142220 | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 | 42222 | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W | 142221 | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | 42223 | [8 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 | 42224 | CT1 TYPE |  | Config | enum16 | R/W | 142223 | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 | 42225 | CT1 PHASE SHIFT | Deg | Config | float32 | R/W | 142224 | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | 42226 | [8 empty] | element |  |  | ALL
CH1 CT Sign | 2226 | 42227 | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W | 142226 | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 | 42228 | CT2 RANGE | A | Config | float32 | R/W | 142227 | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | 42229 | [8 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 | 42230 | Voltage Reference for CT2 |  | Config | enum16 | R/W | 142229 | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 | 42231 | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W | 142230 | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | 42232 | [8 empty] | element | >0 |  | ALL
CH2 CT type | 2232 | 42233 | CT2 TYPE |  | Config | enum16 | R/W | 142232 | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 | 42234 | CT2 PHASE SHIFT | Deg | Config | float32 | R/W | 142233 | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | 42235 | [8 empty] | element |  |  | ALL
CH2 CT Sign | 2235 | 42236 | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W | 142235 | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 | 42237 | CT3 INTEGER | A | Config | float32 | R/W | 142236 | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | 42238 | [8 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 | 42239 | Voltage Reference for CT3 |  | Config | enum16 | R/W | 142238 | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 | 42240 | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W | 142239 | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | 42241 | [8 empty] | element | >0 |  | ALL
CH3 CT type | 2241 | 42242 | CT3 TYPE |  | Config | enum16 | R/W | 142241 | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 | 42243 | CT3 PHASE SHIFT | Deg | Config | float32 | R/W | 142242 | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | 42244 | [8 empty] | element |  |  | ALL
CH3 CT Sign | 2244 | 42245 | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W | 142244 | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 | 42246 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 | 42247 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 | 42248 | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 | 42249 | PF Sign Convention |  | Config | uint16 | R/W | 2248 | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 | 42250 | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 | 42251 | BACnet UDP Port |  | Config | uint16 | R/W | 2250 | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 | 42252 | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 | 42253 | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | 42254 | [8 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 | 42261 | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | 42262 | [11 empty] | ALL
BACnet Max Info Frames | 2262 | 42263 | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 | 42264 | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 | 42265 | BBMD IP Address |  | Config | string(16) | R/W | 2264 | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | 42266 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | 42267 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | 42268 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | 42269 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | 42270 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | 42271 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | 42272 | [9 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 | 42273 | LCD/WebApp Read Password |  | Config | uint16 | R/W | 2272 | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 | 42274 | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 | 42275 | Customer Line frequency |  | Config | float | R/W | 2274 | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | 42276 | [10 empty] | Reserved | ALL
Communications Interface Configured | 2276 | 42277 | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 | 42278 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 | 42279 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 | 42280 | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 | 42281 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 | 42282 | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 | 42283 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 | 42284 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 | 42285 | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 | 42286 | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 | 42287 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 | 42288 | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 | 42289 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 | 42290 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 | 42291 | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 | 42292 | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | 42293 | [11 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 | 42294 | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | 42295 | [11 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 | 42296 | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 | 42297 | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - | METROLOGY POINTS | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 | 42301 | Displacement PF Avg Element | dPF | Metrology | float32 | R | 142300 | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | 42302 | [11 empty] | ALL
Displacement PF CH1 (MSW) | 2302 | 42303 | Displacement PF CH1 (A) | dPF | Metrology | float32 | R | 142302 | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | 42304 | [11 empty] | ALL
Displacement PF CH2 (MSW) | 2304 | 42305 | Displacement PF CH2 (B) | dPF | Metrology | float32 | R | 142304 | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | 42306 | [11 empty] | ALL
Displacement PF CH3 (MSW) | 2306 | 42307 | Displacement PF CH3 (C) | dPF | Metrology | float32 | R | 142306 | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | 42308 | [11 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 | 42309 | Avg Apparent PF Element | aPF | Metrology | float32 | R | 142308 | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | 42310 | [11 empty] | ALL
Apparent PF CH1 (MSW) | 2310 | 42311 | Apparent PF CH1 (A) | aPF | Metrology | float32 | R | 142310 | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | 42312 | [11 empty] | ALL
Apparent PF CH2 (MSW) | 2312 | 42313 | Apparent PF CH2 (B) | aPF | Metrology | float32 | R | 142312 | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | 42314 | [11 empty] | ALL
Apparent PF CH3 (MSW) | 2314 | 42315 | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R | 142314 | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | 42316 | [11 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 | 42317 | Distortion PF Avg Element | tPF | Metrology | float32 | R | 142316 | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | 42318 | [11 empty] | ALL
Distortion PF CH1 (MSW) | 2318 | 42319 | Distortion PF CH1 (A) | tPF | Metrology | float32 | R | 142318 | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | 42320 | [11 empty] | ALL
Distortion PF CH2 (MSW) | 2320 | 42321 | Distortion PF CH2 (B) | tPF | Metrology | float32 | R | 142320 | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | 42322 | [11 empty] | ALL
Distortion PF CH3 (MSW) | 2322 | 42323 | Distortion PF CH3 (C) | tPF | Metrology | float32 | R | 142322 | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | 42324 | [11 empty] | ALL
THD Avg Element (MSW) | 2324 | 42325 | THD Avg Element | % | Metrology | float32 | R | 142324 | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | 42326 | [11 empty] | ALL
THD CH1 (MSW) | 2326 | 42327 | THD CH1 (A) | % | Metrology | float32 | R | 142326 | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | 42328 | [11 empty] | ALL
THD CH2 (MSW) | 2328 | 42329 | THD CH2 (B) | % | Metrology | float32 | R | 142328 | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | 42330 | [11 empty] | ALL
THD CH3 (MSW) | 2330 | 42331 | THD CH3 (C) | % | Metrology | float32 | R | 142330 | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | 42332 | [11 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 | 42333 | Power Demand Max Interval Element | kW | Metrology | float32 | R | 142332 | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | 42334 | [11 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 | 42335 | Power Demand This Interval Element | kW | Metrology | float32 | R | 142334 | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | 42336 | [11 empty] | ALL
VA Peak Demand Element (MSW) | 2336 | 42337 | VA Demand Max Interval Element | kVA | Metrology | float32 | R | 142336 | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | 42338 | [11 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 | 42339 | VA Demand This Interval Element | kVA | Metrology | float32 | R | 142338 | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | 42340 | [11 empty] | ALL
Not Used | 2340 | 42341 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 | 42342 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 | 42343 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 | 42344 | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 | 42345 | Energy Net Sum Element | kWh | Metrology | float32 | R | 142344 | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | 42346 | [8 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 | 42347 | Energy Net CH1 | kWh | Metrology | float32 | R | 142346 | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | 42348 | [8 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 | 42349 | Energy Net CH2 | kWh | Metrology | float32 | R | 142348 | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | 42350 | [8 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 | 42351 | Energy Net CH3 | kWh | Metrology | float32 | R | 142350 | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | 42352 | [8 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 | 42353 | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R | 142352 | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | 42354 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 | 42355 | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R | 142354 | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | 42356 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 | 42357 | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R | 142356 | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | 42358 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 | 42359 | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R | 142358 | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | 42360 | [8 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 | 42361 | VARh Net Sum Element | kVArh | Metrology | float32 | R | 142360 | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | 42362 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 | 42363 | VARh Net CH1 | kVArh | Metrology | float32 | R | 142362 | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | 42364 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 | 42365 | VARh Net CH2 | kVArh | Metrology | float32 | R | 142364 | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | 42366 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 | 42367 | VARh Net CH3 | kVArh | Metrology | float32 | R | 142366 | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | 42368 | [8 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 | 42369 | Time Since Reset MSW | Sec | Metrology | uint32 |  | 2368 | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 | 42370 | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 | 42371 | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 | 42372 | CH1 Angle | Deg | Metrology | float32 | R | 142371 | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | 42373 | [8 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 | 42374 | CH2 Angle | Deg | Metrology | float32 | R | 142373 | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | 42375 | [8 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 | 42376 | CH3 Angle | Deg | Metrology | float32 | R | 142375 | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | 42377 | [11 empty] | ALL
Phase Chek System Status | 2377 | 42378 | System Phase Check Status |  | Metrology | bitfield16 | R | 2377 | BV | Phase Check System Status | system | 0,1 | 0 (All Channels OK), 1(Somewhere a channel is reading a dPF < 0.55), check register 2378 for each Element | ALL
Phase Chek Element Status | 2378 | 42379 | Element Phase Check Status |  | Metrology | bitfield16 | R | 142378 | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 | 42380 | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 | 42381 | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 | 42382 | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 | 42392 | Element Angle |  | Metrology | float | R | 142391 | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | 42393 | [11 empty] | ALL
PULSE INPUTS | - | - | PULSE INPUTS | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 | 42401 | Pulse Input 1 Enable |  | Config | uint16 | R/W | 2400 | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 | 42402 | Pulse Input 1 Scale Factor |  | Config | float32 | R/W | 2401 | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 | 42403 |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 | 42404 | Pulse Input 1 Units |  | Config | string(4) | R/W | 2403 | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 | 42405 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 | 42406 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 | 42407 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 | 42408 | Pulse Input 1 Accumulator |  | Metrology | float32 | R | 2407 | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | 42409 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 | 42410 | Pulse Input 1 Accumulator Clear |  | User | unit16 | W | 2409 | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 | 42411 | Pulse Input 2 Enable |  | Config | uint16 | R/W | 2410 | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 | 42412 | Pulse Input 2 Scale Factor |  | Config | float32 | R/W | 2411 | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | 42413 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 | 42414 | Pulse Input 2 Units |  | Config | string(4) | R/W | 2413 | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 | 42415 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 | 42416 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 | 42417 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 | 42418 | Pulse Input 2 Accumulator |  | Metrology | float32 | R | 2417 | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | 42419 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 | 42420 | Pulse Input 2 Accumulator Clear |  | User | unit16 | W | 2419 | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 | 42421 | Pulse Input 3 Enable |  | Config | uint16 | R/W | 2420 | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 | 42422 | Pulse Input 3 Scale Factor |  | Config | float32 | R/W | 2421 | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | 42423 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 | 42424 | Pulse Input 3 Units |  | Config | string(4) | R/W | 2423 | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 | 42425 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 | 42426 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 | 42427 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 | 42428 | Pulse Input 3 Accumulator |  | Metrology | float32 | R | 2427 | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | 42429 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 | 42430 | Pulse Input 3 Accumulator Clear |  | User |  | W | 2429 | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 | 42431 | Pulse Input 4 Enable |  | Config | uint16 | R/W | 2430 | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 | 42432 | Pulse Input 4 Scale Factor |  | Config | float32 | R/W | 2431 | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | 42433 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 | 42434 | Pulse Input 4 Units |  | Config | string(4) | R/W | 2433 | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 | 42435 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 | 42436 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 | 42437 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 | 42438 | Pulse Input 4 Accumulator |  | Metrology | float32 | R | 2437 | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | 42439 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 | 42440 | Pulse Input 4 Accumulator Clear |  | User | unit16 | W | 2439 | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - | ALARMS | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 | 42452 | State of Alarm |  | Metrology | uint16 | R/W | 2451 | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 | 42453 | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 | 42454 | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 | 42455 | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 | 42456 | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 | 42457 | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 | 42458 | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 | 42459 | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W | 2458 | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 | 42460 | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W | 2459 | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Range Vin1 L1N Under | 2460 | 42461 | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W | 2460 | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 | 42462 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2N Under | 2462 | 42463 | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W | 2462 | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 | 42464 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3N Under | 2464 | 42465 | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W | 2464 | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 | 42466 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L1L2 Under | 2466 | 42467 | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W | 2466 | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 | 42468 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2L3 Under | 2468 | 42469 | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W | 2468 | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 | 42470 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3L1 Under | 2470 | 42471 | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W | 2470 | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 | 42472 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin2 L1N Under | 2472 | 42473 | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W | 2472 | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 | 42474 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2N Under | 2474 | 42475 | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W | 2474 | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 | 42476 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3N Under | 2476 | 42477 | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W | 2476 | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 | 42478 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L1L2 Under | 2478 | 42479 | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W | 2478 | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 | 42480 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2L3 Under | 2480 | 42481 | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W | 2480 | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 | 42482 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3L1 Under | 2482 | 42483 | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W | 2482 | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 | 42484 | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 | 42485 | Voltage Alarm Persistence | Sec | Config | uint16 | R/W | 2484 | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 | 42486 | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R | 2485 | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 | 42487 | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 | 42488 | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R | 2487 | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 | 42489 | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 | 42490 | Real Time Clock MSW |  | Config | uint16 | R/W | 2489 | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 | 42491 | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - | USER CONFIG POINTS 2 | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 | 42602 | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 | 42603 | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 | 42604 | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 | 42605 | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 | 42606 | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 | 42607 | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 | 42608 | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 | 42609 | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 | 42610 | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 | 42611 | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 | 42612 | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 | 42613 | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 | 42614 | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 | 42615 | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 | 42616 | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 | 42617 | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 | 42618 | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 | 42619 | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 | 42620 | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 | 42621 | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 | 42622 | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 | 42623 | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 | 42624 | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 | 42625 | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 | 42626 | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 | 42627 | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 | 42628 | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 | 42629 | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 | 42630 | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 | 42631 | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 | 42632 | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 | 42633 | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 | 42634 | BACnet Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | 2634 | 42635 | BACnet Description 1 | [8 empty] | 2 Char |  | ALL
BACnet Description 2 | 2635 | 42636 | BACnet Description 2 | [8 empty] | 2 Char |  | ALL
BACnet Description 3 | 2636 | 42637 | BACnet Description 3 | [8 empty] | 2 Char |  | ALL
BACnet Description 4 | 2637 | 42638 | BACnet Description 4 | [8 empty] | 2 Char |  | ALL
BACnet Description 5 | 2638 | 42639 | BACnet Description 5 | [8 empty] | 2 Char |  | ALL
BACnet Description 6 | 2639 | 42640 | BACnet Description 6 | [8 empty] | 2 Char |  | ALL
BACnet Description 7 | 2640 | 42641 | BACnet Description 7 | [8 empty] | 2 Char |  | ALL
BACnet Description 8 | 2641 | 42642 | BACnet Description 8 | [8 empty] | 2 Char |  | ALL
BACnet Description 9 | 2642 | 42643 | BACnet Description 9 | [8 empty] | 2 Char |  | ALL
BACnet Description 10 | 2643 | 42644 | BACnet Description 10 | [8 empty] | 2 Char |  | ALL
BACnet Description 11 | 2644 | 42645 | BACnet Description 11 | [8 empty] | 2 Char |  | ALL
BACnet Description 12 | 2645 | 42646 | BACnet Description 12 | [8 empty] | 2 Char |  | ALL
BACnet Description 13 | 2646 | 42647 | BACnet Description 13 | [8 empty] | 2 Char |  | ALL
BACnet Description 14 | 2647 | 42648 | BACnet Description 14 | [8 empty] | 2 Char |  | ALL
BACnet Description 15 | 2648 | 42649 | BACnet Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
VERIS EMULATION LEGACY REGISTERS | - | - | VERIS EMULATION LEGACY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Veris Emulation Mode | 2200 | 42201 | Set to Veris Emulation Mode |  | Config | uint16 | R/W |  |  |  | system | 0-1 | 1 = Report Slave ID as Veris Model H8036 | ALL
kWh System LSW | 0 | 40001 | kWh System LSW | kWh | Veris | uint32 | R |  |  |  | element |  |  | ALL
kWh System MSW | 1 | 40002 | kWh System MSW | kWh | Veris |  | R |  |  |  | element |  |  | ALL
kW System | 2 | 40003 | kW System | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVAR System | 3 | 40004 | kVAR System | kVAR | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVA System | 4 | 40005 | kVA System | kVA | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF System | 5 | 40006 | Apparent PF System | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts Line to Line Avg | 6 | 40007 | Volts Line to Line Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts Line to Neutral Avg | 7 | 40008 | Volts Line to Neutral Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps System Avg | 8 | 40009 | Amps System Avg | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L1 | 9 | 40010 | kW L1 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L2 | 10 | 40011 | kW L2 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L3 | 11 | 40012 | kW L3 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L1 | 12 | 40013 | Apparent PF L1 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L2 | 13 | 40014 | Apparent PF L2 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L3 | 14 | 40015 | Apparent PF L3 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts L1 to L2 | 15 | 40016 | Volts L1 to L2 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to L3 | 16 | 40017 | Volts L2 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to L3 | 17 | 40018 | Volts L1 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to Neutral | 18 | 40019 | Volts L1 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to Neutral | 19 | 40020 | Volts L2 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L3 to Neutral | 20 | 40021 | Volts L3 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps L1 | 21 | 40022 | Amps L1 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L2 | 22 | 40023 | Amps L2 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L3 | 23 | 40024 | Amps L3 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW System Avg | 24 | 40025 | kW System Avg | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Now | 25 | 40026 | kW Demand Sys Now (was Min) | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Max | 26 | 40027 | kW Demand Sys Max | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL

## P
1
REGISTER POINT LIST
MODBUS SLAVE RELATIVE ADDRESS --> | 16
BACNET OBJECT FLOOR --> | 150000
Modbus Register Name | Modbus Register | Absolute Address | Item Description | Units | Functionality | Data Type | R/W | BACnet Object | BACnet Object Type | BACnet Object Name | System or Element | Value/Range | Public Notes | Models
SunSpec C001 Common Model | - | - | SunSpec Common Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec Model ID LSW | 1001 | 41002 | SunSpec Model (SunS) 1 |  |  | uint32 | R |  |  |  | system | Su (0x5375) |  | ALL
SunSpec Model ID MSW | 1002 | 41003 | [8 empty] | system | nS (0x6E53) |  | ALL
SunSpec Device ID | 1003 | 41004 | Unique SunSpec Model Identifier (1) |  |  | unit16 | R |  |  |  | system | 1 |  | ALL
Model Length | 1004 | 41005 | Model Length (66) |  |  | unit16 | R |  |  |  | system | 66 |  | ALL
Manufacturer 0 | 1005 | 41006 | Manufacturer Name (string) |  | Factory | string(16) | R | Dev Obj Prop |  |  | system | 2 Char | Factory Set | ALL
Manufacturer 1 | 1006 | 41007 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 2 | 1007 | 41008 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 3 | 1008 | 41009 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 4 | 1009 | 41010 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 5 | 1010 | 41011 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 6 | 1011 | 41012 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 7 | 1012 | 41013 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 8 | 1013 | 41014 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 9 | 1014 | 41015 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 10 | 1015 | 41016 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 11 | 1016 | 41017 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 12 | 1017 | 41018 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 13 | 1018 | 41019 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 14 | 1019 | 41020 | [8 empty] | system | 2 Char |  | ALL
Manufacturer 15 | 1020 | 41021 | [8 empty] | system | 1 Char NULL |  | ALL
Model 0 | 1021 | 41022 | Model Name (Model Number) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
Model 1 | 1022 | 41023 | [8 empty] | system | 2 Char |  | ALL
Model 2 | 1023 | 41024 | [8 empty] | system | 2 Char |  | ALL
Model 3 | 1024 | 41025 | [8 empty] | system | 2 Char |  | ALL
Model 4 | 1025 | 41026 | [8 empty] | system | 2 Char |  | ALL
Model 5 | 1026 | 41027 | [8 empty] | system | 2 Char |  | ALL
Model 6 | 1027 | 41028 | [8 empty] | system | 2 Char |  | ALL
Model 7 | 1028 | 41029 | [8 empty] | system | 2 Char |  | ALL
Model 8 | 1029 | 41030 | [8 empty] | system | 2 Char |  | ALL
Model 9 | 1030 | 41031 | [8 empty] | system | 2 Char |  | ALL
Model 10 | 1031 | 41032 | [8 empty] | system | 2 Char |  | ALL
Model 11 | 1032 | 41033 | [8 empty] | system | 2 Char |  | ALL
Model 12 | 1033 | 41034 | [8 empty] | system | 2 Char |  | ALL
Model 13 | 1034 | 41035 | [8 empty] | system | 2 Char |  | ALL
Model 14 | 1035 | 41036 | [8 empty] | system | 2 Char |  | ALL
Model 15 | 1036 | 41037 | [8 empty] | system | 1 Char NULL |  | ALL
Options 0 | 1037 | 41038 | Options |  | Future | string(8) | R |  |  |  | system | 2 Char |  | ALL
Options 1 | 1038 | 41039 | [8 empty] | system | 2 Char |  | ALL
Options 2 | 1039 | 41040 | [8 empty] | system | 2 Char |  | ALL
Options 3 | 1040 | 41041 | [8 empty] | system | 2 Char |  | ALL
Options 4 | 1041 | 41042 | [8 empty] | system | 2 Char |  | ALL
Options 5 | 1042 | 41043 | [8 empty] | system | 2 Char |  | ALL
Options 6 | 1043 | 41044 | [8 empty] | system | 2 Char |  | ALL
Options 7 | 1044 | 41045 | [8 empty] | system | 1 Char NULL |  | ALL
Version 0 | 1045 | 41046 | Firmware Version |  | Factory | string(8) | R |  |  |  | system | 2 Char |  | ALL
Version 1 | 1046 | 41047 | [8 empty] | system | 2 Char |  | ALL
Version 2 | 1047 | 41048 | [8 empty] | system | 2 Char |  | ALL
Version 3 | 1048 | 41049 | [8 empty] | system | 2 Char |  | ALL
Version 4 | 1049 | 41050 | [8 empty] | system | 2 Char |  | ALL
Version 5 | 1050 | 41051 | [8 empty] | system | 2 Char |  | ALL
Version 6 | 1051 | 41052 | [8 empty] | system | 2 Char |  | ALL
Version 7 | 1052 | 41053 | [8 empty] | system | 1 Char NULL |  | ALL
SerialNumber 0 | 1053 | 41054 | Serial Number(xxxYYMMNNN) |  | Factory | string(16) | R |  |  |  | system | 2 Char | Factory Set | ALL
SerialNumber 1 | 1054 | 41055 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 2 | 1055 | 41056 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 3 | 1056 | 41057 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 4 | 1057 | 41058 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 5 | 1058 | 41059 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 6 | 1059 | 41060 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 7 | 1060 | 41061 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 8 | 1061 | 41062 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 9 | 1062 | 41063 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 10 | 1063 | 41064 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 11 | 1064 | 41065 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 12 | 1065 | 41066 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 13 | 1066 | 41067 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 14 | 1067 | 41068 | [8 empty] | system | 2 Char |  | ALL
SerialNumber 15 | 1068 | 41069 | [8 empty] | system | 1 Char NULL |  | ALL
Dev Addr | 1069 | 41070 | Modbus Device Address |  |  | unit16 | R/W | 1069 | PIV | SERIAL ADDRESS | system | 1 - 245 |  | ALL
Common Pad | 1070 | 41071 | [8 empty] | system | 0 |  | ALL
SunSpec NC016 TCP Network Stack Model | - | - | TCP Network Stack | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC016 MODEL ID | 1071 | 41072 | SunSpec Model (016) |  |  | unit16 | R |  |  |  | system | 16 (0x10) |  | ALL
NC016 MODEL LENGTH | 1072 | 41073 | Model Length (52) |  |  | unit16 | R |  |  |  | system | 52 (0x34) |  | ALL
NC016 INTERFACE NAME 0 | 1073 | 41074 | Interface name |  |  | string(4) | R |  |  |  | system | ET (0x4554) |  | ALL
NC016 INTERFACE NAME 1 | 1074 | 41075 | [8 empty] | system | H0 (0x4830) |  | ALL
NC016 INTERFACE NAME 2 | 1075 | 41076 | [8 empty] | system | 0 |  | ALL
NC016 INTERFACE NAME 3 | 1076 | 41077 | [8 empty] | system | 0 |  | ALL
DHCP/STATIC CONFIG | 1077 | 41078 | Enum for force IPV4 config method (0=static/1=DHCP) |  |  | enum16 | R/W | 1077 | BV | DHCP/STATIC CONFIG | system | 1 |  | ALL
NTP/DNS CONTROL | 1078 | 41079 | Bitmask value configure use of services (0=DNS/1=NTP) |  |  | enum16 | R/W |  |  |  | system | 0 |  | ALL
IP ADDRESS 0 | 1079 | 41080 | IP Address |  |  | string(8) | R/W | 1079 | CSV | IP Address | system | 2 Char |  | ALL
IP ADDRESS 1 | 1080 | 41081 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 2 | 1081 | 41082 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 3 | 1082 | 41083 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 4 | 1083 | 41084 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 5 | 1084 | 41085 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 6 | 1085 | 41086 | [8 empty] | system | 2 Char |  | ALL
IP ADDRESS 7 | 1086 | 41087 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
NETMASK 0 | 1087 | 41088 | Netmask |  |  | string(8) | R/W | 1087 | CSV | IP Netmask | system | 2 Char |  | ALL
NETMASK 1 | 1088 | 41089 | [8 empty] | system | 2 Char |  | ALL
NETMASK 2 | 1089 | 41090 | [8 empty] | system | 2 Char |  | ALL
NETMASK 3 | 1090 | 41091 | [8 empty] | system | 2 Char |  | ALL
NETMASK 4 | 1091 | 41092 | [8 empty] | system | 2 Char |  | ALL
NETMASK 5 | 1092 | 41093 | [8 empty] | system | 2 Char |  | ALL
NETMASK 6 | 1093 | 41094 | [8 empty] | system | 2 Char |  | ALL
NETMASK 7 | 1094 | 41095 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
GATEWAY 0 | 1095 | 41096 | Gateway |  |  | string(8) | R/W | 1095 | CSV | IP Gateway | system | 2 Char |  | ALL
GATEWAY 1 | 1096 | 41097 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 2 | 1097 | 41098 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 3 | 1098 | 41099 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 4 | 1099 | 41100 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 5 | 1100 | 41101 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 6 | 1101 | 41102 | [8 empty] | system | 2 Char |  | ALL
GATEWAY 7 | 1102 | 41103 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS1 ADDRESS 0 | 1103 | 41104 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS1 ADDRESS 1 | 1104 | 41105 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 2 | 1105 | 41106 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 3 | 1106 | 41107 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 4 | 1107 | 41108 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 5 | 1108 | 41109 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 6 | 1109 | 41110 | [8 empty] | system | 2 Char |  | ALL
DNS1 ADDRESS 7 | 1110 | 41111 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
DNS2 ADDRESS 0 | 1111 | 41112 | 32 bit IP address of DNS server |  |  | string(8) | R/W |  |  |  | system | 2 Char |  | ALL
DNS2 ADDRESS 1 | 1112 | 41113 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 2 | 1113 | 41114 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 3 | 1114 | 41115 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 4 | 1115 | 41116 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 5 | 1116 | 41117 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 6 | 1117 | 41118 | [8 empty] | system | 2 Char |  | ALL
DNS2 ADDRESS 7 | 1118 | 41119 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
MAC ADDRESS 0 | 1119 | 41120 | IEEE MAC address of this interface |  |  | unit64 | R |  |  |  | system | 0 |  | ALL
MAC ADDRESS 1 | 1120 | 41121 | [8 empty] | system | 0x000D |  | ALL
MAC ADDRESS 2 | 1121 | 41122 | [8 empty] | system | 0x633x | x=1 (PS48), x=2(PS12), x=3 (PS3), x=4 (PS24) | ALL
MAC ADDRESS 3 | 1122 | 41123 | [8 empty] | system | unit # |  | ALL
LINK CONTROL | 1123 | 41124 | Bitmask value link control flags |  |  |  | R |  |  |  | system | 3 |  | ALL
PAD | 1124 | 41125 | [9 empty] | 0 |  | ALL
SunSpec NC017 Serial Interface Model | - | - | Serial Interface Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec NC017 MODEL ID | 1125 | 41126 | SunSpec Model (017) |  |  | unit16 | R |  |  |  | system | 17 |  | ALL
NC017 MODEL LENGTH | 1126 | 41127 | Model Length (12) |  |  | unit16 | R |  |  |  | system | 12 |  | ALL
NC017 INTERFACE NAME 0 | 1127 | 41128 | Interface name |  |  | string(4) | R/W |  |  |  | system | 2 Char |  | ALL
NC017 INTERFACE NAME 1 | 1128 | 41129 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 2 | 1129 | 41130 | [8 empty] | system | 2 Char |  | ALL
NC017 INTERFACE NAME 3 | 1130 | 41131 | [8 empty] | system | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
SERIAL BAUD RATE MSW | 1131 | 41132 | Interface baud rate in bits per second |  |  | uint32 | R/W | 1131 | PIV | Serial Baudrate | system | 9600 - 115k |  | ALL
SERIAL BAUD RATE LSW | 1132 | 41133 | [8 empty] | system |  |  | ALL
SERIAL BITS | 1133 | 41134 | Number of data bits per character |  |  | enum16 | R/W |  |  |  | system | 8 |  | ALL
SERIAL PARITY | 1134 | 41135 | Bitmask value - parity setting |  |  | enum16 | R/W |  |  |  | system | 0-2 |  | ALL
SERIAL DUPLEX | 1135 | 41136 | Enumerated value - duplex mode |  |  | enum16 | R/W |  |  |  | system | 0-1 |  | ALL
SERIAL FLOW CONTROL | 1136 | 41137 | Flow control method |  |  | enum16 | R/W |  |  |  | system | 0-2 | (0 = none, 1 = Odd, 2 = Even) | ALL
SERIAL INTERFACE TYPE | 1137 | 41138 | Enumerated value - interface type |  |  | enum16 | R |  |  |  | system | 2 |  | ALL
SERIAL PROTOCOL SELECTION | 1138 | 41139 | Enumerated value - serial protocol selection |  |  | enum16 | R |  |  |  | system | 1 |  | ALL
SunSpec 213 Wye Float Model | - | - | Wye Float Model | - | - | - | - | - | - | - | - | - | - | -
SunSpec 213 MODEL ID | 1139 | 41140 | SunSpec Model (213) |  |  | unit16 | R |  |  |  | system | 213 (0xD5) |  | ALL
SunSpec 213 MODEL LENGTH | 1140 | 41141 | Model Length (124) |  |  | unit16 | R |  |  |  | system | 124 (0x7C) |  | ALL
Current Avg Element (MSW) | 1141 | 41142 | Current Avg Element | A | Metrology | float32 | R | 151141 | AI | Current Avg Element | element |  | Average current of enabled channels | ALL
Current Avg Element (LSW) | 1142 | 41143 | [8 empty] | element |  |  | ALL
Current CH1 (MSW) | 1143 | 41144 | Current CH1 (A) | A | Metrology | float32 | R | 151143 | AI | Current CH1 | element |  | RMS | ALL
Current CH1 (LSW) | 1144 | 41145 | [8 empty] | element |  |  | ALL
Current CH2 (MSW) | 1145 | 41146 | Current CH2 (B) | A | Metrology | float32 | R | 151145 | AI | Current CH2 | element |  | RMS | ALL
Current CH2 (LSW) | 1146 | 41147 | [8 empty] | element |  |  | ALL
Current CH3 (MSW) | 1147 | 41148 | Current CH3 (C) | A | Metrology | float32 | R | 151147 | AI | Current CH3 | element |  | RMS | ALL
Current CH3 (LSW) | 1148 | 41149 | [8 empty] | element |  |  | ALL
Voltage L to N Avg Element (MSW) | 1149 | 41150 | Voltage L to N Avg Element | V | Metrology | float32 | R | 151149 | AI | Voltage L to N Avg Element | element |  | Voltage (AN+BN+CN)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to N Avg Element (LSW) | 1150 | 41151 | [8 empty] | element |  |  | ALL
Voltage L1 to N (MSW) | 1151 | 41152 | Voltage L1 to N (AN) | V | Metrology | float32 | R | 151151 | AI | Voltage L1 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to N (LSW) | 1152 | 41153 | [8 empty] | element |  |  | ALL
Voltage L2 to N (MSW) | 1153 | 41154 | Voltage L2 to N (BN) | V | Metrology | float32 | R | 151153 | AI | Voltage L2 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to N (LSW) | 1154 | 41155 | [8 empty] | element |  |  | ALL
Voltage L3 to N (MSW) | 1155 | 41156 | Voltage L3 to N (CN) | V | Metrology | float32 | R | 151155 | AI | Voltage L3 to N | element |  | RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to N (LSW) | 1156 | 41157 | [8 empty] | element |  |  | ALL
Voltage L to L Avg Element (MSW) | 1157 | 41158 | Voltage L to L Avg Element | V | Metrology | float32 | R | 151157 | AI | Voltage L to L Avg Element | element |  | (AB+BC+CA)/3 (VREF is selected per element in Reg 2217) | ALL
Voltage L to L Avg Element (LSW) | 1158 | 41159 | [8 empty] | element |  |  | ALL
Voltage L1 to L2 (MSW) | 1159 | 41160 | Voltage L1 to L2 (AB) | V | Metrology | float32 | R | 151159 | AI | Voltage L1 to L2 | element |  | AN-BN RMS (Vref selected by Reg 2217) | ALL
Voltage L1 to L2 (LSW) | 1160 | 41161 | [8 empty] | element |  |  | ALL
Voltage L2 to L3 (MSW) | 1161 | 41162 | Voltage L2 to L3 (BC) | V | Metrology | float32 | R | 151161 | AI | Voltage L2 to L3 | element |  | BN-CN RMS (Vref selected by Reg 2217) | ALL
Voltage L2 to L3 (LSW) | 1162 | 41163 | [8 empty] | element |  |  | ALL
Voltage L3 to L1 (MSW) | 1163 | 41164 | Voltage L3 to L1 (CA) | V | Metrology | float32 | R | 151163 | AI | Voltage L3 to L1 | element |  | CN-AN RMS (Vref selected by Reg 2217) | ALL
Voltage L3 to L1 (LSW) | 1164 | 41165 | [8 empty] | element |  |  | ALL
Line Frequency (MSW) | 1165 | 41166 | Line Frequency | Hz | Metrology | float32 | R | 151165 | AI | Line Frequency | element | 45 - 70 | Can take up to 10 seconds to respond to abrupt change in service frequency | ALL
Line Frequency (LSW) | 1166 | 41167 | [8 empty] | element |  |  | ALL
Watt Sum Element (MSW) | 1167 | 41168 | Power Sum Element | kW | Metrology | float32 | R | 151167 | AI | Power Sum Element | element |  | Power_A+Power_B+Power_C | ALL
Watt Sum Element (LSW) | 1168 | 41169 | [8 empty] | element |  |  | ALL
Watt CH1 (MSW) | 1169 | 41170 | Power CH1 (A) | kW | Metrology | float32 | R | 151169 | AI | Power CH1 | element |  | Signed Power | ALL
Watt CH1 (LSW) | 1170 | 41171 | [8 empty] | element |  |  | ALL
Watt CH2 (MSW) | 1171 | 41172 | Power CH2 (B) | kW | Metrology | float32 | R | 151171 | AI | Power CH2 | element |  | Signed Power | ALL
Wattr CH2 (LSW) | 1172 | 41173 | [8 empty] | element |  |  | ALL
Watt CH3 (MSW) | 1173 | 41174 | Power CH3 (C) | kW | Metrology | float32 | R | 151173 | AI | Power CH3 | element |  | Signed Power | ALL
Watt CH3 (LSW) | 1174 | 41175 | [8 empty] | element |  |  | ALL
VA Sum Element (MSW) | 1175 | 41176 | VA Sum Element | kVA | Metrology | float32 | R | 151175 | AI | VA Sum Element | element |  | VA_A+VA_B+VA_C | ALL
VA Sum Element (LSW) | 1176 | 41177 | [8 empty] | element |  |  | ALL
VA CH1 (MSW) | 1177 | 41178 | VA CH1 (A) | kVA | Metrology | float32 | R | 151177 | AI | VA CH1 | element |  | Signed VA | ALL
VA CH1 (LSW) | 1178 | 41179 | [8 empty] | element |  |  | ALL
VA CH2 (MSW) | 1179 | 41180 | VA CH2 (B) | kVA | Metrology | float32 | R | 151179 | AI | VA CH2 | element |  | Signed VA | ALL
VA CH2 (LSW) | 1180 | 41181 | [8 empty] | element |  |  | ALL
VA CH3 (MSW) | 1181 | 41182 | VA CH3 (C) | kVA | Metrology | float32 | R | 151181 | AI | VA CH3 | element |  | Signed VA | ALL
VA CH3 (LSW) | 1182 | 41183 | [8 empty] | element |  |  | ALL
VAR Sum Element (MSW) | 1183 | 41184 | VAR Sum Element | kVAr | Metrology | float32 | R | 151183 | AI | VAR Sum Element | element |  | VAR_A+VAR_B+VAR_C | ALL
VAR Sum Element (LSW) | 1184 | 41185 | [8 empty] | element |  |  | ALL
VAR CH1 (MSW) | 1185 | 41186 | VAR CH1 (A) | kVAr | Metrology | float32 | R | 151185 | AI | VAR CH1 | element |  | Signed VAR | ALL
VAR CH1 (LSW) | 1186 | 41187 | [8 empty] | element |  |  | ALL
VAR CH2 (MSW) | 1187 | 41188 | VAR CH2 (B) | kVAr | Metrology | float32 | R | 151187 | AI | VAR CH2 | element |  | Signed VAR | ALL
VAR CH2 (LSW) | 1188 | 41189 | [8 empty] | element |  |  | ALL
VAR CH3 (MSW) | 1189 | 41190 | VAR CH3 (C) | kVAr | Metrology | float32 | R | 151189 | AI | VAR CH3 | element |  | Signed VAR | ALL
VAR CH3 (LSW) | 1190 | 41191 | [8 empty] | element |  |  | ALL
Apparent PF Avg Element (MSW) | 1191 | 41192 | Apparent PF Avg Element | PF | Metrology | float32 | R | 151191 | AI | Apparent PF Avg Element | element |  | (PF CH1 (A) + PF CH2 (B) + PF CH3 (C) )/ 3 | ALL
Apparent PF Avg Element (LSW) | 1192 | 41193 | [8 empty] | element |  |  | ALL
Apparent PF CH1 (MSW) | 1193 | 41194 | Apparent PF CH1 (A) | PF | Metrology | float32 | R | 151193 | AI | Apparent PF CH1 | element |  | Apparent_PF_A | ALL
Apparent PF CH1 (LSW) | 1194 | 41195 | [8 empty] | element |  |  | ALL
Apparent PF CH2 (MSW) | 1195 | 41196 | Apparent PF CH2 (B) | PF | Metrology | float32 | R | 151195 | AI | Apparent PF CH2 | element |  | Apparent_PF_B | ALL
Apparent PF CH2 (LSW) | 1196 | 41197 | [8 empty] | element |  |  | ALL
Apparent PF CH3 (MSW) | 1197 | 41198 | Apparent PF CH3 ( C) | PF | Metrology | float32 | R | 151197 | AI | Apparent PF CH3 | element |  | Apparent_PF_C | ALL
Apparent PF CH3 (LSW) | 1198 | 41199 | [8 empty] | element |  |  | ALL
Exported Energy Sum Element (MSW) | 1199 | 41200 | Exported Energy Sum Element | kWh | Metrology | float32 | R | 151199 | AI | Exported Energy Sum Element | element |  | Total Energy Expported (CH1 + CH2 + CH3) | ALL
Exported Energy Sum Element (LSW) | 1200 | 41201 | [8 empty] | element |  |  | ALL
Exported Energy CH1 (MSW) | 1201 | 41202 | Exported Energy CH1 (A) | kWh | Metrology | float32 | R | 151201 | AI | Exported Energy CH1 | element |  | Source Power | ALL
Exported Energy CH1 (LSW) | 1202 | 41203 | [8 empty] | element |  |  | ALL
Exported Energy CH2 (MSW) | 1203 | 41204 | Exported Energy CH2 (B) | kWh | Metrology | float32 | R | 151203 | AI | Exported Energy CH2 | element |  | Source Power | ALL
Exported Energy CH2 (LSW) | 1204 | 41205 | [8 empty] | element |  |  | ALL
Exported Energy CH3 (MSW) | 1205 | 41206 | Exported Energy CH3 (C) | kWh | Metrology | float32 | R | 151205 | AI | Exported Energy CH3 | element |  | Source Power | ALL
Exported Energy CH3 (LSW) | 1206 | 41207 | [8 empty] | element |  |  | ALL
Imported Energy Sum Element (MSW) | 1207 | 41208 | Imported Energy Sum Element | kWh | Metrology | float32 | R | 151207 | AI | Imported Energy Sum Element | element |  | Total Energy Imported (CH1 + CH2 + CH3) | ALL
Imported Energy Sum Element (LSW) | 1208 | 41209 | [8 empty] | element |  |  | ALL
Imported Energy CH1 (MSW) | 1209 | 41210 | Imported Energy CH1 (A) | kWh | Metrology | float32 | R | 151209 | AI | Imported Energy CH1 | element |  | Load Power | ALL
Imported Energy CH1 (LSW) | 1210 | 41211 | [8 empty] | element |  |  | ALL
Imported Energy CH2 (MSW) | 1211 | 41212 | Imported Energy CH2 (B) | kWh | Metrology | float32 | R | 151211 | AI | Imported Energy CH2 | element |  | Load Power | ALL
Imported Energy CH2 (LSW) | 1212 | 41213 | [8 empty] | element |  |  | ALL
Imported Energy CH3 (MSW) | 1213 | 41214 | Imported Energy CH3 (C) | kWh | Metrology | float32 | R | 151213 | AI | Imported Energy CH3 | element |  | Load Power | ALL
Imported Energy CH3 (LSW) | 1214 | 41215 | [8 empty] | element |  |  | ALL
Exported VAh Sum Element (MSW) | 1215 | 41216 | Exported VAh Sum Element | kVAh | Metrology | float32 | R | 151215 | AI | Exported VAh Sum Element | element |  | Total Exported VAh (CH1 + CH2 + CH3) | ALL
Exported VAh Sum Element (LSW) | 1216 | 41217 | [8 empty] | element |  |  | ALL
Exported VAh CH1 (MSW) | 1217 | 41218 | Exported VAh CH1 (A) | kVAh | Metrology | float32 | R | 151217 | AI | Exported VAh CH1 | element |  | Source Apparent Energy | ALL
Exported VAh CH1 (LSW) | 1218 | 41219 | [8 empty] | element |  |  | ALL
Exported VAh CH2 (MSW) | 1219 | 41220 | Exported VAh CH2 (B) | kVAh | Metrology | float32 | R | 151219 | AI | Exported VAh CH2 | element |  | Source Apparent Energy | ALL
Exported VAh CH2 (LSW) | 1220 | 41221 | [8 empty] | element |  |  | ALL
Exported VAh CH3 (MSW) | 1221 | 41222 | Exported VAh CH3 (C) | kVAh | Metrology | float32 | R | 151221 | AI | Exported VAh CH3 | element |  | Source Apparent Energy | ALL
Exported VAh CH3 (LSW) | 1222 | 41223 | [8 empty] | element |  |  | ALL
Imported VAh Sum Element (MSW) | 1223 | 41224 | Imported VAh Sum Element | kVAh | Metrology | float32 | R | 151223 | AI | Imported VAh Sum Element | element |  | Total Imported VAh (CH1 + CH2 + CH3) | ALL
Imported VAh Sum Element (LSW) | 1224 | 41225 | [8 empty] | element |  |  | ALL
Imported VAh CH1 (MSW) | 1225 | 41226 | Imported VAh CH1 (A) | kVAh | Metrology | float32 | R | 151225 | AI | Imported VAh CH1 | element |  | Load Apparent Energy | ALL
Imported VAh CH1 (LSW) | 1226 | 41227 | [8 empty] | element |  |  | ALL
Imported VAh CH2 (MSW) | 1227 | 41228 | Imported VAh CH2 (B) | kVAh | Metrology | float32 | R | 151227 | AI | Imported VAh CH2 | element |  | Load Apparent Energy | ALL
Imported VAh CH2 (LSW) | 1228 | 41229 | [8 empty] | element |  |  | ALL
Imported VAh CH3 (MSW) | 1229 | 41230 | Imported VAh CH3 (C) | kVAh | Metrology | float32 | R | 151229 | AI | Imported VAh CH3 | element |  | Load Apparent Energy | ALL
Imported VAh CH3 (LSW) | 1230 | 41231 | [8 empty] | element |  |  | ALL
Imported VARh Q1 Sum Element (MSW) | 1231 | 41232 | Imported VARh Q1 Sum Element | kVArh | Metrology | float32 | R | 151231 | AI | Imported VARh Q1 Sum Element | element |  | Total Imported VARh in Q1 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q1 Sum Element (LSW) | 1232 | 41233 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH1 (MSW) | 1233 | 41234 | Imported VARh Q1 CH1 (A) | kVArh | Metrology | float32 | R | 151233 | AI | Imported VARh Q1 CH1 | element |  | Load Postive Reactive Energy | ALL
Imported VARh Q1 CH1 (LSW) | 1234 | 41235 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH2 (MSW) | 1235 | 41236 | Imported VARh Q1 CH2 (B) | kVArh | Metrology | float32 | R | 151235 | AI | Imported VARh Q1 CH2 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH2 (LSW) | 1236 | 41237 | [8 empty] | element |  |  | ALL
Imported VARh Q1 CH3 (MSW) | 1237 | 41238 | Imported VARh Q1 CH3 (C) | kVArh | Metrology | float32 | R | 151237 | AI | Imported VARh Q1 CH3 | element |  | Load Positive Reactive Energy | ALL
Imported VARh Q1 CH3 (LSW) | 1238 | 41239 | [8 empty] | element |  |  | ALL
Imported VARh Q2 Sum Element (MSW) | 1239 | 41240 | Imported VARh Q2 Sum Element | kVArh | Metrology | float32 | R | 151239 | AI | Imported VARh Q2 Sum Element | element |  | Total Imported VARh in Q2 (Ch1 + Ch2 + Ch3) | ALL
Imported VARh Q2 Sum Element (LSW) | 1240 | 41241 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH1 (MSW) | 1241 | 41242 | Imported VARh Q2 CH1 (A) | kVArh | Metrology | float32 | R | 151241 | AI | Imported VARh Q2 CH1 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH1 (LSW) | 1242 | 41243 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH2 (MSW) | 1243 | 41244 | Imported VARh Q2 CH2 (B) | kVArh | Metrology | float32 | R | 151243 | AI | Imported VARh Q2 CH2 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH2 (LSW) | 1244 | 41245 | [8 empty] | element |  |  | ALL
Imported VARh Q2 CH3 (MSW) | 1245 | 41246 | Imported VARh Q2 CH3 (C) | kVArh | Metrology | float32 | R | 151245 | AI | Imported VARh Q2 CH3 | element |  | Source Positive Reactive Energy | ALL
Imported VARh Q2 CH3 (LSW) | 1246 | 41247 | [8 empty] | element |  |  | ALL
Exported VARh Q3 Sum Element (MSW) | 1247 | 41248 | Exported VARh Q3 Sum Element | kVArh | Metrology | float32 | R | 151247 | AI | Exported VARh Q3 Sum Element | element |  | Total Exported VARh in Q3 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q3 Sum Element (LSW) | 1248 | 41249 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH1 (MSW) | 1249 | 41250 | Exported VARh Q3 CH1 (A) | kVArh | Metrology | float32 | R | 151249 | AI | Exported VARh Q3 CH1 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH1 (LSW) | 1250 | 41251 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH2 (MSW) | 1251 | 41252 | Exported VARh Q3 CH2 (B) | kVArh | Metrology | float32 | R | 151251 | AI | Exported VARh Q3 CH2 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH2 (LSW) | 1252 | 41253 | [8 empty] | element |  |  | ALL
Exported VARh Q3 CH3 (MSW) | 1253 | 41254 | Exported VARh Q3 CH3 (C) | kVArh | Metrology | float32 | R | 151253 | AI | Exported VARh Q3 CH3 | element |  | Source Negative Reactive Energy | ALL
Exported VARh Q3 CH3 (LSW) | 1254 | 41255 | [8 empty] | element |  |  | ALL
Exported VARh Q4 Sum Element (MSW) | 1255 | 41256 | Exported VARh Q4 Sum Element | kVArh | Metrology | float32 | R | 151255 | AI | Exported VARh Q4 Sum Element | element |  | Total Exported VARh in Q4 (Ch1 + Ch2 + Ch3) | ALL
Exported VARh Q4 Sum Element (LSW) | 1256 | 41257 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH1 (MSW) | 1257 | 41258 | Exported VARh Q4 CH1 (A) | kVArh | Metrology | float32 | R | 151257 | AI | Exported VARh Q4 CH1 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH1 (LSW) | 1258 | 41259 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH2 (MSW) | 1259 | 41260 | Exported VARh Q4 CH2 (B) | kVArh | Metrology | float32 | R | 151259 | AI | Exported VARh Q4 CH2 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH2 (LSW) | 1260 | 41261 | [8 empty] | element |  |  | ALL
Exported VARh Q4 CH3 (MSW) | 1261 | 41262 | Exported VARh Q4 CH3 © | kVArh | Metrology | float32 | R | 151261 | AI | Exported VARh Q4 CH3 | element |  | Load Negative Reactive Energy | ALL
Exported VARh Q4 CH3 (LSW) | 1262 | 41263 | [8 empty] | element |  |  | ALL
Events MSW | 1263 | 41264 | Events MSW |  |  | bitfield32 | R | 1263 | AI | Events | system |  |  | ALL
Events LSW | 1264 | 41265 | Events LSW | [7 empty] | system |  |  | ALL
SUNSPEC_M_DID_END | 1265 | 41266 | Sunspec Device ID END (0xFFFF) |  |  | uint16 | R |  |  |  | element |  |  | ALL
SUNSPEC_M_Length_END | 1266 | 41267 | Sunspec Length end (0) |  |  | uint16 | R |  |  |  | element |  |  | ALL
FACTORY REGISTERS | - | - | FACTORY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Factory Unlock Register | 2000 | 42001 | Factory Unlock Register |  | Factory | unit16 | R/W |  |  |  | system |  | Reserved | ALL
Factory Reset | 2001 | 42002 | Factory Reset |  | Factory | unit16 | R/W |  |  |  | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
OEM Vendor ID | 2002 | 42003 | OEM Vendor ID |  | Factory | unit16 | R |  |  |  | system |  | Reserved | ALL
FACTORY_CONFIG | 2003 | 42004 | Factory Config |  | Factory | unit16 | R |  |  |  | system | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable | ALL
USER COMMAND POINTS | - | - | USER COMMAND POINTS | - | - | - | - | - | - | - | - | - | - | -
Reset Processor | 2100 | 42101 | Reset (software) processor |  | User | unit16 | W | 2100 | BV | Reset Processor | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements All | 2101 | 42102 | Clear all accumulated measurements (CAM) |  | User | unit16 | W | 2101 | BV | Clear Accumulated Measurements All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Accumulated Measurements Element | 2102 | 42103 | Clear Accumulated Measurements Element (CAM) |  | User | unit16 | W | 152102 | BV | Clear Accumulated Measurements Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand Element | 2103 | 42104 | Clear Peak Demand Element |  | User | unit16 | W | 152103 | BV | Clear Peak Demand Element | element | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Clear Peak Demand All | 2104 | 42105 | Clear Peak Demand All |  | User | unit16 | W | 2104 | BV | Clear Peak Demand All | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
Reset to User Defaults | 2105 | 42106 | Reset to User Defaults |  | User | unit16 | W | 2105 | BV | Reset to User Defaults | system | 1 or 1234 | Modbus Reset Command (1234), or BACnet Reset Command (1) | ALL
USER CONFIG POINTS | - | - | USER CONFIG POINTS | - | - | - | - | - | - | - | - | - | - | -
Demand Window Type | 2201 | 42202 | Sliding or Fixed |  | Config | enum16 | R | 2201 | MSV | Demand Window Type | system | 1-2 | Currently Sliding Mode Only | ALL
Demand Window | 2202 | 42203 | Demand Window | Min | Config | uint16 | R | 2202 | PIV | Demand Window Length | system | 15 | Currently set to 15 minutes | ALL
Volt Multiplier VINPUT1 (MSW) | 2203 | 42204 | Volt Multiplier VINPUT1 |  | Config | float32 | R/W | 2203 | AV | Volt Multiplier VINPUT1 | system | >0 | Used with Potential Transformer | ALL
Volt Multiplier VINPUT1 (LSW) | 2204 | 42205 | [8 empty] | system | >0 |  | ALL
Volt Multiplier VINPUT2 (MSW) | 2205 | 42206 | Volt Multiplier VINPUT2 |  | Config | float32 | R/W | 2205 | AV | Volt Multiplier VINPUT2 | system | >0 | Used with Potential Transformer | PS 24 / 48
Volt Multiplier VINPUT2 (LSW) | 2206 | 42207 | [8 empty] | system | >0 |  | PS 24 / 48
Service Type Element | 2207 | 42208 | Service Type |  | Config | enum16 | R/W | 152207 | MSV | Service Type Element | element | 1-5 | (4Wire 3Φ=1), 3Wire 3Φ=2,3Wire 1Φ=3,2Wire 1Φ=4, OFF=5) | ALL
Millivolt Snap Threshold (MSW) | 2208 | 42209 | Snap MV Threshold | PER | Config | float32 | R/W | 2208 | AV | Millivolt Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
Millivolt Snap Threshold (LSW) | 2209 | 42210 | [8 empty] | system |  |  | ALL
RoCoil Snap Threshold (MSW) | 2210 | 42211 | Snap Rog Threshold | PER | Config | float32 | R/W | 2210 | AV | RoCoil Snap Threshold | system | >= 0 | Report 0 rather than values below this % of full scale CT , use with caution | ALL
RoCoil Snap Threshold (LSW) | 2211 | 42212 | [8 empty] | system |  |  | ALL
Voltage Snap Threshold (MSW) | 2212 | 42213 | Snap Volt Threshold | V | Config | float32 | R/W | 2212 | AV | Voltage Snap Threshold | system | >= 0 | Report 0 rather than values below this absolute voltage , use with caution | ALL
Voltage Snap Threshold (LSW) | 2213 | 42214 | [8 empty] | system |  |  | ALL
Communications Mode | 2214 | 42215 | Communications Mode |  | Config |  |  | 2214 | MSV | Communications Mode | system | 1-2 | 1 (Modbus), 2 (BACnet) - Applicable for RS-485 Communications | ALL
RoCoil Millivolt per Kiloamp (MSW) | 2215 | 42216 | RoCoil Millivolt per Kiloamp (MSW) |  | Config | float32 | R/W | 2215 | AV | RoCoil Millivolt per Kiloamp | system | 50-1000 | Gain at 60 HZ, use with caution (preset to 131) | ALL
RoCoil Millivolt per Kiloamp (LSW) | 2216 | 42217 | [8 empty] | system |  |  | ALL
Voltage Input Element | 2217 | 42218 | Element Voltage Input |  | Config | enum16 | R/W | 152217 | MSV | Voltage Input | element | 1-2 |  | PS 24 / 48
CH1 CT Full Scale Rating (MSW) | 2218 | 42219 | CT1 RANGE | A | Config | float32 | R/W | 152218 | AV | CH1 CT Full Scale Rating | element | >0 |  | ALL
CH1 CT Full Scale Rating (LSW) | 2219 | 42220 | [8 empty] | element | >0 |  | ALL
CH1 CT Voltage Reference | 2220 | 42221 | Voltage Reference for CT1 |  | Config | enum16 | R/W | 152220 | MSV | CH1 CT Voltage Reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH1 CT Multiplier (MSW) | 2221 | 42222 | CT1 AMPS MULTIPLIER |  | Config | float32 | R/W | 152221 | AV | CH1 CT Multiplier | element | >0 |  | ALL
CH1 CT Multiplier (LSW) | 2222 | 42223 | [8 empty] | element | >0 |  | ALL
CH1 CT Type | 2223 | 42224 | CT1 TYPE |  | Config | enum16 | R/W | 152223 | PIV | CH1 CT Type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH1 CT Phase Shift (MSW) | 2224 | 42225 | CT1 PHASE SHIFT | Deg | Config | float32 | R/W | 152224 | AV | CH1 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH1 CT Phase Shift (LSW) | 2225 | 42226 | [8 empty] | element |  |  | ALL
CH1 CT Sign | 2226 | 42227 | FLIP THE SIGN OF CT 1 READING |  |  | uint16 | R/W | 152226 | BV | CH1 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH2 CT Full Scale Rating (MSW) | 2227 | 42228 | CT2 RANGE | A | Config | float32 | R/W | 152227 | AV | CH2 CT Full Scale Rating | element | >0 |  | ALL
CH2 CT Full Scale Rating (LSW) | 2228 | 42229 | [8 empty] | element | >0 |  | ALL
CH2 CT Voltage Reference | 2229 | 42230 | Voltage Reference for CT2 |  | Config | enum16 | R/W | 152229 | MSV | CH2 CT Volts reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH2 CT Multiplier (MSW) | 2230 | 42231 | CT2 AMPS MULTIPLIER |  | Config | float32 | R/W | 152230 | AV | CH2 CT Multiplier | element | >0 |  | ALL
CH2 CT Multiplier (LSW) | 2231 | 42232 | [8 empty] | element | >0 |  | ALL
CH2 CT type | 2232 | 42233 | CT2 TYPE |  | Config | enum16 | R/W | 152232 | PIV | CH2 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH2 CT Phase Shift (MSW) | 2233 | 42234 | CT2 PHASE SHIFT | Deg | Config | float32 | R/W | 152233 | AV | CH2 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH2 CT Phase Shift (LSW) | 2234 | 42235 | [8 empty] | element |  |  | ALL
CH2 CT Sign | 2235 | 42236 | FLIP THE SIGN OF CT 2 READING |  | Config | uint16 | R/W | 152235 | BV | CH2 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
CH3 CT Full Scale Rating (MSW) | 2236 | 42237 | CT3 INTEGER | A | Config | float32 | R/W | 152236 | AV | CH3 CT Full Scale Rating | element | >0 |  | ALL
CH3 CT Full Scale Rating (LSW) | 2237 | 42238 | [8 empty] | element | >0 |  | ALL
CH3 CT Voltage Reference | 2238 | 42239 | Voltage Reference for CT3 |  | Config | enum16 | R/W | 152238 | MSV | CH3 CT volt reference | element | 1-6 | (L1-N=1, L2-N=2, L3-N=3, L1-L2=4, L2-L3=5, L3-L1=6) | ALL
CH3 CT amps multiplier (MSW) | 2239 | 42240 | CT3 AMPS MULTIPLIER |  | Config | float32 | R/W | 152239 | AV | CH3 CT Multiplier | element | >0 |  | ALL
CH3 CT amps multiplier (LSW) | 2240 | 42241 | [8 empty] | element | >0 |  | ALL
CH3 CT type | 2241 | 42242 | CT3 TYPE |  | Config | enum16 | R/W | 152241 | PIV | CH3 CT type | element | 0-2 | 0 (OFF), 1 (mV), 2 (RoCoil) | ALL
CH3 CT Phase Shift (MSW) | 2242 | 42243 | CT3 PHASE SHIFT | Deg | Config | float32 | R/W | 152242 | AV | CH3 CT Phase Shift | element | -4.0˚ to +4.0˚ |  | ALL
CH3 CT Phase Shift (LSW) | 2243 | 42244 | [8 empty] | element |  |  | ALL
CH3 CT Sign | 2244 | 42245 | FLIP THE SIGN OF CT 3 READING |  | Config | uint16 | R/W | 152244 | BV | CH3 CT Flipper | element | 0-1 | 0(NORMAL), 1(REVERSED) | ALL
Not Used | 2245 | 42246 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2246 | 42247 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2247 | 42248 | Not Used | [9 empty] | Reserved | ALL
PF Sign Convention | 2248 | 42249 | PF Sign Convention |  | Config | uint16 | R/W | 2248 | MSV | PF Sign Convention | system | 1-2 | 1 (ANSI),2 (IEEE) | ALL
Modbus TCP Port | 2249 | 42250 | Modbus TCP Port |  |  |  | R |  |  |  | system | 502 |  | ALL
BACnet UDP Port | 2250 | 42251 | BACnet UDP Port |  | Config | uint16 | R/W | 2250 | PIV | UDP Port | system |  |  | ALL
Not Used | 2251 | 42252 | Not Used | [9 empty] | Legacy Enable Element (Behavior covered by Register 2207 with value of 5) | ALL
BACnet Vendor ID (MSW) | 2252 | 42253 | BACnet Vendor ID |  | Config | uint32 | R | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Vendor ID (LSW) | 2253 | 42254 | [8 empty] | system |  |  | ALL
BACnet Device ID (MSW) | 2260 | 42261 | BACnet Device ID |  | Config | uint32 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BACnet Device ID (LSW) | 2261 | 42262 | [11 empty] | ALL
BACnet Max Info Frames | 2262 | 42263 | BACnet Max Info Frames |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
Bacnet Max Masters | 2263 | 42264 | Bacnet Max Masters |  | Config | uint16 | R/W | Dev Obj Prop |  |  | system |  |  | ALL
BBMD IP Address 0 | 2264 | 42265 | BBMD IP Address |  | Config | string(16) | R/W | 2264 | CSV | BBMD IP Address | system | 2 Char |  | ALL
BBMD IP Address 1 | 2265 | 42266 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 2 | 2266 | 42267 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 3 | 2267 | 42268 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 4 | 2268 | 42269 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 5 | 2269 | 42270 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 6 | 2270 | 42271 | [9 empty] | 2 Char |  | ALL
BBMD IP Address 7 | 2271 | 42272 | [9 empty] | 1 CHAR NULL | Meter String Block Updated Upon Write to Final Character | ALL
LCD/WebApp Read Password | 2272 | 42273 | LCD/WebApp Read Password |  | Config | uint16 | R/W | 2272 | PIV | LCD/WebApp Read Password | system |  | Encoded PIN | ALL
LCD/WebApp Read/Write Password | 2273 | 42274 | LCD/WebApp Read/Write Password |  | Config | uint16 | R/W | 2273 | PIV | LCD/WebApp Read/Write Password | system |  | Encoded PIN | ALL
Customer Line frequency (MSW) | 2274 | 42275 | Customer Line frequency |  | Config | float | R/W | 2274 | AV | Line Frequency Expected | system |  | Reserved | ALL
Customer Line frequency (LSW) | 2275 | 42276 | [10 empty] | Reserved | ALL
Communications Interface Configured | 2276 | 42277 | Communications Interface Configured |  | Config | uint16 | R/W |  |  |  | system |  | Reserved | ALL
Not Used | 2277 | 42278 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2278 | 42279 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2279 | 42280 | Not Used | [9 empty] | Legacy Pulse_Output1_Acc_Type | ALL
Not Used | 2280 | 42281 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2281 | 42282 | Not Used | [9 empty] | Legacy Pulse_Output1_Manual_Value | ALL
Not Used | 2282 | 42283 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_MSW | ALL
Not Used | 2283 | 42284 | Not Used | [9 empty] | Legacy Pulse_Output1_Energy_LSW | ALL
Not Used | 2284 | 42285 | Not Used | [9 empty] | Legcay Pulse_Output1_Type | ALL
Not Used | 2285 | 42286 | Not Used | [9 empty] | Legacy Pulse_Output2_Acc_Type | ALL
Not Used | 2286 | 42287 | Not Used | [9 empty] | Legacy Pulse_Output1_Source_Element_Num | ALL
Not Used | 2287 | 42288 | Not Used | [9 empty] | Legacy Pulse_Output2_Manual_Value | ALL
Not Used | 2288 | 42289 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_MSW | ALL
Not Used | 2289 | 42290 | Not Used | [9 empty] | Legacy Pulse_Output2_Energy_LSW | ALL
Not Used | 2290 | 42291 | Not Used | [9 empty] | Legacy Pulse_Output2_Type | ALL
VOLTAGE_CONV_CONSTANT (MSW) | 2291 | 42292 | Voltage conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
VOLTAGE_CONV_CONSTANT (LSW) | 2292 | 42293 | [11 empty] | ALL
CURRENT_CONV_CONSTANT (MSW) | 2293 | 42294 | Current conversion constant - ADC to Engg unit |  | Config |  | R | [5 empty] | Reserved | ALL
CURRENT_CONV_CONSTANT (LSW) | 2294 | 42295 | [11 empty] | ALL
COMMUNICATION INACTIVITY TIMEOUT | 2295 | 42296 | Processor Reset Period Under Loss Of Communications | Min | Config | uint16 | R/W |  |  |  | System | 0-65535 | Reset Processor if no comms are detected for N minutes (0 is disabled) | ALL
USER_CONFIG | 2296 | 42297 | User Config to enable/disable features |  | Config | uint16 | R/W |  |  |  | System | 0-255 | BIT (0) Web App Enable, BIT (1) UDP Discovery Enable. | ALL
METROLOGY POINTS | - | - | METROLOGY POINTS | - | - | - | - | - | - | - | - | - | - | -
Displacement PF Avg Element (MSW) | 2300 | 42301 | Displacement PF Avg Element | dPF | Metrology | float32 | R | 152300 | AI | Displacement PF Avg Element | element |  | Element KW / SQRT ( Element KW^2 + Element VAR^2) | ALL
Displacement PF Avg Element (LSW) | 2301 | 42302 | [11 empty] | ALL
Displacement PF CH1 (MSW) | 2302 | 42303 | Displacement PF CH1 (A) | dPF | Metrology | float32 | R | 152302 | AI | Displacement PF CH1 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH1 (LSW) | 2303 | 42304 | [11 empty] | ALL
Displacement PF CH2 (MSW) | 2304 | 42305 | Displacement PF CH2 (B) | dPF | Metrology | float32 | R | 152304 | AI | Displacement PF CH2 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH2 (LSW) | 2305 | 42306 | [11 empty] | ALL
Displacement PF CH3 (MSW) | 2306 | 42307 | Displacement PF CH3 (C) | dPF | Metrology | float32 | R | 152306 | AI | Displacement PF CH3 | element |  | CH KW / SQRT ( CH KW^2 + CH VAR^2) | ALL
Displacement PF CH3 (LSW) | 2307 | 42308 | [11 empty] | ALL
Apparent PF Avg Element (MSW) | 2308 | 42309 | Avg Apparent PF Element | aPF | Metrology | float32 | R | 152308 | AI | Apparent PF Avg Element | element |  | Element Power / Element VA | ALL
Apparent PF Avg Element (LSW) | 2309 | 42310 | [11 empty] | ALL
Apparent PF CH1 (MSW) | 2310 | 42311 | Apparent PF CH1 (A) | aPF | Metrology | float32 | R | 152310 | AI | Apparent PF CH1 | element |  | (Duplicate of Reg # 1193) | ALL
Apparent PF CH1 (LSW) | 2311 | 42312 | [11 empty] | ALL
Apparent PF CH2 (MSW) | 2312 | 42313 | Apparent PF CH2 (B) | aPF | Metrology | float32 | R | 152312 | AI | Apparent PF CH2 | element |  | (Duplicate of Reg # 1195) | ALL
Apparent PF CH2 (LSW) | 2313 | 42314 | [11 empty] | ALL
Apparent PF CH3 (MSW) | 2314 | 42315 | Apparent PF CH3 ( C) | aPF | Metrology | float32 | R | 152314 | AI | Apparent PF CH3 | element |  | (Duplicate of Reg # 1197) | ALL
Apparent PF CH3 (LSW) | 2315 | 42316 | [11 empty] | ALL
Distortion PF Avg Element (MSW) | 2316 | 42317 | Distortion PF Avg Element | tPF | Metrology | float32 | R | 152316 | AI | Distortion PF Avg Element | element |  | Computed as Element aPF / Element dPF | ALL
Distortion PF Avg Element (LSW) | 2317 | 42318 | [11 empty] | ALL
Distortion PF CH1 (MSW) | 2318 | 42319 | Distortion PF CH1 (A) | tPF | Metrology | float32 | R | 152318 | AI | Distortion PF CH1 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH1 (LSW) | 2319 | 42320 | [11 empty] | ALL
Distortion PF CH2 (MSW) | 2320 | 42321 | Distortion PF CH2 (B) | tPF | Metrology | float32 | R | 152320 | AI | Distortion PF CH2 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH2 (LSW) | 2321 | 42322 | [11 empty] | ALL
Distortion PF CH3 (MSW) | 2322 | 42323 | Distortion PF CH3 (C) | tPF | Metrology | float32 | R | 152322 | AI | Distortion PF CH3 | element |  | Computed as CH aPF / CH dPF | ALL
Distortion PF CH3 (LSW) | 2323 | 42324 | [11 empty] | ALL
THD Avg Element (MSW) | 2324 | 42325 | THD Avg Element | % | Metrology | float32 | R | 152324 | AI | THD Avg Element | element |  | Computed Element THD | ALL
THD Avg Element (LSW) | 2325 | 42326 | [11 empty] | ALL
THD CH1 (MSW) | 2326 | 42327 | THD CH1 (A) | % | Metrology | float32 | R | 152326 | AI | THD CH1 | element |  | Computed CH THD on Power | ALL
THD CH1 (LSW) | 2327 | 42328 | [11 empty] | ALL
THD CH2 (MSW) | 2328 | 42329 | THD CH2 (B) | % | Metrology | float32 | R | 152328 | AI | THD CH2 | element |  | Computed CH THD on Power | ALL
THD CH2 (LSW) | 2329 | 42330 | [11 empty] | ALL
THD CH3 (MSW) | 2330 | 42331 | THD CH3 (C) | % | Metrology | float32 | R | 152330 | AI | THD CH3 | element |  | Computed CH THD on Power | ALL
THD CH3 (LSW) | 2331 | 42332 | [11 empty] | ALL
Watt Peak Demand Element (MSW) | 2332 | 42333 | Power Demand Max Interval Element | kW | Metrology | float32 | R | 152332 | AI | Power Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Peak Demand Element (LSW) | 2333 | 42334 | [11 empty] | ALL
Watt Demand This Interval Element (MSW) | 2334 | 42335 | Power Demand This Interval Element | kW | Metrology | float32 | R | 152334 | AI | Power Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
Watt Demand This Interval Element (LSW) | 2335 | 42336 | [11 empty] | ALL
VA Peak Demand Element (MSW) | 2336 | 42337 | VA Demand Max Interval Element | kVA | Metrology | float32 | R | 152336 | AI | VA Demand Max Interval Element | element |  | Calculated from Imported Energy | ALL
VA Peak Demand Element (LSW) | 2337 | 42338 | [11 empty] | ALL
VA Demand This Interval Element (MSW) | 2338 | 42339 | VA Demand This Interval Element | kVA | Metrology | float32 | R | 152338 | AI | VA Demand This Interval Element | element |  | Calculated from Imported Energy | ALL
VA Demand This Interval Element (MSW) | 2339 | 42340 | [11 empty] | ALL
Not Used | 2340 | 42341 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2341 | 42342 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2342 | 42343 | Not Used | [9 empty] | Reserved | ALL
Not Used | 2343 | 42344 | Not Used | [9 empty] | Reserved | ALL
Active Energy Net Sum Element (MSW) | 2344 | 42345 | Energy Net Sum Element | kWh | Metrology | float32 | R | 152344 | AI | Energy Net Sum Element | element |  | Total Watt-hours Imported (1207) - Total Watt-hours Exported (1199) | ALL
Active Energy Net Sum Element (LSW) | 2345 | 42346 | [8 empty] | element |  |  | ALL
Active Energy Net CH1 (MSW) | 2346 | 42347 | Energy Net CH1 | kWh | Metrology | float32 | R | 152346 | AI | Energy Net CH1 | element |  | Total Watt-hours Imported phase A (1209) - Total Watt-hours Exported phase A (1201) | ALL
Active Energy Net CH1 (LSW) | 2347 | 42348 | [8 empty] | element |  |  | ALL
Active Energy Net CH2 (MSW) | 2348 | 42349 | Energy Net CH2 | kWh | Metrology | float32 | R | 152348 | AI | Energy Net CH2 | element |  | Total Watt-hours Imported phase B (1211) - Total Watt-hours Exported phase B (1203) | ALL
Active Energy Net CH2 (LSW) | 2349 | 42350 | [8 empty] | element |  |  | ALL
Active Energy Net CH3 (MSW) | 2350 | 42351 | Energy Net CH3 | kWh | Metrology | float32 | R | 152350 | AI | Energy Net CH3 | element |  | Total Watt-hours Imported phase C (1213) - Total Watt-hours Exported phase C (1205) | ALL
Active Energy Net CH3 (LSW) | 2351 | 42352 | [8 empty] | element |  |  | ALL
Apparent Energy Net Sum Element (MSW) | 2352 | 42353 | Apparent Energy Net Sum Element | kVAh | Metrology | float32 | R | 152352 | AI | Apparent Energy Net Sum Element | element |  | Total VA-hours Imported (1223) - Total VA-hours Exported (1215) | ALL
Apparent Energy Net Sum Element (LSW) | 2353 | 42354 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH1 (MSW) | 2354 | 42355 | Apparent Energy Net CH1 | kVAh | Metrology | float32 | R | 152354 | AI | Apparent Energy Net CH1 | element |  | Total VA-hours Imported phase A (1225) - Total VA-hours Exported phase A (1217) | ALL
Apparent Energy Net CH1 (LSW) | 2355 | 42356 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH2 (MSW) | 2356 | 42357 | Apparent Energy Net CH2 | kVAh | Metrology | float32 | R | 152356 | AI | Apparent Energy Net CH2 | element |  | Total VA-hours Imported phase B (1227) - Total Watt-hours Exported phase B (1219) | ALL
Apparent Energy Net CH2 (LSW) | 2357 | 42358 | [8 empty] | element |  |  | ALL
Apparent Energy Net CH3 (MSW) | 2358 | 42359 | Apparent Energy Net CH3 | kVAh | Metrology | float32 | R | 152358 | AI | Apparent Energy Net CH3 | element |  | Total VA-hours Imported phase C (1229) - Total VA-hours Exported phase C (1221) | ALL
Apparent Energy Net CH3 (LSW) | 2359 | 42360 | [8 empty] | element |  |  | ALL
Reactive Energy Net Sum Element (MSW) | 2360 | 42361 | VARh Net Sum Element | kVArh | Metrology | float32 | R | 152360 | AI | VARh Net Sum Element | element |  | Total VAR-hours Imported (1231+1239) - Total VAR-hours Exported (1247+1255) | ALL
Reactive Energy Net Sum Element (LSW) | 2361 | 42362 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH1 (MSW) | 2362 | 42363 | VARh Net CH1 | kVArh | Metrology | float32 | R | 152362 | AI | VARh Net CH1 | element |  | Total VAR-hours Imported (1233+1241) - Total VAR-hours Exported (1249+1257) | ALL
Reactive Energy Net CH1 (LSW) | 2363 | 42364 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH2 (MSW) | 2364 | 42365 | VARh Net CH2 | kVArh | Metrology | float32 | R | 152364 | AI | VARh Net CH2 | element |  | Total VAR-hours Imported (1235+1243) - Total VAR-hours Exported (1251+1259) | ALL
Reactive Energy Net CH2 (LSW) | 2365 | 42366 | [8 empty] | element |  |  | ALL
Reactive Energy Net CH3 (MSW) | 2366 | 42367 | VARh Net CH3 | kVArh | Metrology | float32 | R | 152366 | AI | VARh Net CH3 | element |  | Total VAR-hours Imported (1237+1245) - Total VAR-hours Exported (1253+1261) | ALL
Reactive Energy Net CH3 (LSW) | 2367 | 42368 | [8 empty] | element |  |  | ALL
Time Since Reset (MSW) | 2368 | 42369 | Time Since Reset MSW | Sec | Metrology | uint32 |  | 2368 | AI | Time Since CAM | system |  | Time Since Clearing Accumulators | ALL
Time Since Reset (LSW) | 2369 | 42370 | Time Since Reset LSW | Sec | Metrology | [5 empty] | system |  |  | ALL
Not Used | 2370 | 42371 | Not Used | [9 empty] | Legacy Data Acquisition Tick | ALL
Theta CH1 MSW | 2371 | 42372 | CH1 Angle | Deg | Metrology | float32 | R | 152371 | AI | Theta L1 | element |  | CH1 Displacement Angle | ALL
Theta CH1 LSW | 2372 | 42373 | [8 empty] | element |  |  | ALL
Theta CH2 MSW | 2373 | 42374 | CH2 Angle | Deg | Metrology | float32 | R | 152373 | AI | Theta L2 | element |  | CH2 Displacement Angle | ALL
Theta CH2 LSW | 2374 | 42375 | [8 empty] | element |  |  | ALL
Theta CH3 MSW | 2375 | 42376 | CH3 Angle | Deg | Metrology | float32 | R | 152375 | AI | Theta L3 | element |  | CH3 Displacement Angle | ALL
Theta CH3 LSW | 2376 | 42377 | [11 empty] | ALL
Phase Chek System Status | 2377 | 42378 | System Phase Check Status |  | Metrology | bitfield16 | R | 2377 | BV | Phase Check System Status | system | 0,1 | 0 (All Channels OK), 1(Somewhere a channel is reading a dPF < 0.55), check register 2378 for each Element | ALL
Phase Chek Element Status | 2378 | 42379 | Element Phase Check Status |  | Metrology | bitfield16 | R | 152378 | BSV | Element Phase Check Status | element | 0-7 | Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
RoCoil PGA Gain Ch1 | 2379 | 42380 | RoCoil PGA Gain Ch1 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch2 | 2380 | 42381 | RoCoil PGA Gain Ch2 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
RoCoil PGA Gain Ch3 | 2381 | 42382 | RoCoil PGA Gain Ch3 |  | Metrology | uint16 | R |  |  |  | Element |  | Reserved For Future Use | ALL
Theta Element MSW | 2391 | 42392 | Element Angle |  | Metrology | float | R | 152391 | AI | Theta Element | Element |  | Calculated Element Displacement Angle | ALL
Theta Element LSW | 2392 | 42393 | [11 empty] | ALL
PULSE INPUTS | - | - | PULSE INPUTS | - | - | - | - | - | - | - | - | - | - | -
Pulse Input 1 Enable | 2400 | 42401 | Pulse Input 1 Enable |  | Config | uint16 | R/W | 2400 | BV | Pulse Input 1 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 1 Scale Factor | 2401 | 42402 | Pulse Input 1 Scale Factor |  | Config | float32 | R/W | 2401 | AV | Pulse Input 1 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2402 | 42403 |  |  | Config |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Units | 2403 | 42404 | Pulse Input 1 Units |  | Config | string(4) | R/W | 2403 | CSV | Pulse Input 1 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2404 | 42405 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2405 | 42406 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2406 | 42407 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 1 Scale Accumulator | 2407 | 42408 | Pulse Input 1 Accumulator |  | Metrology | float32 | R | 2407 | AI | Pulse Input 1 Accumulator | system |  |  | PS 12 / 24 / 48
| 2408 | 42409 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 1 Accumulator Clear | 2409 | 42410 | Pulse Input 1 Accumulator Clear |  | User | unit16 | W | 2409 | BV | Pulse Input 1 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 2 Enable | 2410 | 42411 | Pulse Input 2 Enable |  | Config | uint16 | R/W | 2410 | BV | Pulse Input 2 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12 / 24 / 48
Pulse Input 2 Scale Factor | 2411 | 42412 | Pulse Input 2 Scale Factor |  | Config | float32 | R/W | 2411 | AV | Pulse Input 2 Scale Factor | system |  |  | PS 12 / 24 / 48
| 2412 | 42413 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Units | 2413 | 42414 | Pulse Input 2 Units |  | Config | string(4) | R/W | 2413 | CSV | Pulse Input 2 Units | system | 2 Char |  | PS 12 / 24 / 48
| 2414 | 42415 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2415 | 42416 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12 / 24 / 48
| 2416 | 42417 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12 / 24 / 48
Pulse Input 2 Scale Accumulator | 2417 | 42418 | Pulse Input 2 Accumulator |  | Metrology | float32 | R | 2417 | AI | Pulse Input 2 Accumulator | system |  |  | PS 12 / 24 / 48
| 2418 | 42419 |  |  |  |  | R |  |  |  | system |  |  | PS 12 / 24 / 48
Pulse Input 2 Accumulator Clear | 2419 | 42420 | Pulse Input 2 Accumulator Clear |  | User | unit16 | W | 2419 | BV | Pulse Input 2 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12 / 24 / 48
Pulse Input 3 Enable | 2420 | 42421 | Pulse Input 3 Enable |  | Config | uint16 | R/W | 2420 | BV | Pulse Input 3 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 3 Scale Factor | 2421 | 42422 | Pulse Input 3 Scale Factor |  | Config | float32 | R/W | 2421 | AV | Pulse Input 3 Scale Factor | system |  |  | PS 12
| 2422 | 42423 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 3 Units | 2423 | 42424 | Pulse Input 3 Units |  | Config | string(4) | R/W | 2423 | CSV | Pulse Input 3 Units | system | 2 Char |  | PS 12
| 2424 | 42425 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2425 | 42426 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2426 | 42427 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 3 Scale Accumulator | 2427 | 42428 | Pulse Input 3 Accumulator |  | Metrology | float32 | R | 2427 | AI | Pulse Input 3 Accumulator | system |  |  | PS 12
| 2428 | 42429 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 3 Accumulator Clear | 2429 | 42430 | Pulse Input 3 Accumulator Clear |  | User |  | W | 2429 | BV | Pulse Input 3 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
Pulse Input 4 Enable | 2430 | 42431 | Pulse Input 4 Enable |  | Config | uint16 | R/W | 2430 | BV | Pulse Input 4 Enable | system | 0,1 | 0 (Off), 1(Enabled) | PS 12
Pulse Input 4 Scale Factor | 2431 | 42432 | Pulse Input 4 Scale Factor |  | Config | float32 | R/W | 2431 | AV | Pulse Input 4 Scale Factor | system |  |  | PS 12
| 2432 | 42433 |  |  |  |  | R/W |  |  |  | system |  |  | PS 12
Pulse Input 4 Units | 2433 | 42434 | Pulse Input 4 Units |  | Config | string(4) | R/W | 2433 | CSV | Pulse Input 4 Units | system | 2 Char |  | PS 12
| 2434 | 42435 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2435 | 42436 |  |  | Config |  | R/W |  |  |  |  | 2 Char |  | PS 12
| 2436 | 42437 |  |  | Config |  | R/W |  |  |  |  | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | PS 12
Pulse Input 4 Scale Accumulator | 2437 | 42438 | Pulse Input 4 Accumulator |  | Metrology | float32 | R | 2437 | AI | Pulse Input 4 Accumulator | system |  |  | PS 12
| 2438 | 42439 |  |  |  |  | R |  |  |  | system |  |  | PS 12
Pulse Input 4 Accumulator Clear | 2439 | 42440 | Pulse Input 4 Accumulator Clear |  | User | unit16 | W | 2439 | BV | Pulse Input 4 Accumulator Clear | system |  | Write a 1 to clear. Can't be read. | PS 12
ALARMS | - | - | ALARMS | - | - | - | - | - | - | - | - | - | - | -
Alarm Output Status | 2451 | 42452 | State of Alarm |  | Metrology | uint16 | R/W | 2451 | BV | Alarm Output Status | system |  | 0 (No alarm) 1 (Alarm triggered), set to 0 to clear | ALL
Not Used | 2452 | 42453 | Not Used |  | Config | bitfield16 | R/W |  |  |  | element |  | Legacy, bitfield for enabeling CT alarms | ALL
Not Used | 2453 | 42454 | Not Used | A | Config | uint16 | R/W |  |  |  | element |  | Legacy, CT Alarm Threshold Under Current | ALL
Not Used | 2454 | 42455 | Not Used | [7 empty] | Element |  | Legacy, Sets High Threshold for All CT's | ALL
Not Used | 2455 | 42456 | Not Used | Sec | Config | uint16 | R/W |  |  |  | element | 3 - 60 | Legacy, Current Alarm Persistence Setting | ALL
Not Used | 2456 | 42457 | Not Used |  | Config | bitfield8 | R |  |  |  | element | 0-7 | Legacy, CT Alarm Status Under Current | ALL
Not Used | 2457 | 42458 | Not Used | [9 empty] | Legacy, Modbus registers are little-endian (CT1 is bit 0, CT2 is bit 1, CT3 is bit 2) BACnet is big-endian (CT1 is bit 7, CT2 is bit 6, CT3 is bit 5) | ALL
Voltage Alarm Vin1 Mask | 2458 | 42459 | Bitfield for all VIN1 and associated phases |  | Config | bitfield8 | R/W | 2458 | BSV | Voltage Alarm Vin1 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Vin2 Mask | 2459 | 42460 | Bitfield for all VIN2 (PS48) and associated phases |  | Config | bitfield8 | R/W | 2459 | BSV | Voltage Alarm Vin2 Mask | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Voltage Alarm Range Vin1 L1N Under | 2460 | 42461 | Voltage Alarm Range Vin1 L1N Under | V | Config | uint16 | R/W | 2460 | PIV | Voltage Alarm Range Vin1 L1N Under | system | 1-385 |  | ALL
Not Used | 2461 | 42462 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2N Under | 2462 | 42463 | Voltage Alarm Range Vin1 L2N Under | V | Config | uint16 | R/W | 2462 | PIV | Voltage Alarm Range Vin1 L2N Under | system | 1-385 |  | ALL
Not Used | 2463 | 42464 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3N Under | 2464 | 42465 | Voltage Alarm Range Vin1 L3N Under | V | Config | uint16 | R/W | 2464 | PIV | Voltage Alarm Range Vin1 L3N Under | system | 1-385 |  | ALL
Not Used | 2465 | 42466 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3N Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L1L2 Under | 2466 | 42467 | Voltage Alarm Range Vin1 L1L2 Under | V | Config | uint16 | R/W | 2466 | PIV | Voltage Alarm Range Vin1 L1L2 Under | system | 1-660 |  | ALL
Not Used | 2467 | 42468 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L1L2 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L2L3 Under | 2468 | 42469 | Voltage Alarm Range Vin1 L2L3 Under | V | Config | uint16 | R/W | 2468 | PIV | Voltage Alarm Range Vin1 L2L3 Under | system | 1-660 |  | ALL
Not Used | 2469 | 42470 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L2L3 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin1 L3L1 Under | 2470 | 42471 | Voltage Alarm Range Vin1 L3L1 Under | V | Config | uint16 | R/W | 2470 | PIV | Voltage Alarm Range Vin1 L3L1 Under | system | 1-660 |  | ALL
Not Used | 2471 | 42472 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin1 L3L1 Over, unsupported beyond firmware 2.07 | ALL
Voltage Alarm Range Vin2 L1N Under | 2472 | 42473 | Voltage Alarm Range Vin2 L1N Under | V | Config | uint16 | R/W | 2472 | PIV | Voltage Alarm Range Vin2 L1N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2473 | 42474 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2N Under | 2474 | 42475 | Voltage Alarm Range Vin2 L2N Under | V | Config | uint16 | R/W | 2474 | PIV | Voltage Alarm Range Vin2 L2N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2475 | 42476 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3N Under | 2476 | 42477 | Voltage Alarm Range Vin2 L3N Under | V | Config | uint16 | R/W | 2476 | PIV | Voltage Alarm Range Vin2 L3N Under | system | 1-660 |  | PS 24 / 48
Not Used | 2477 | 42478 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L3N Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L1L2 Under | 2478 | 42479 | Voltage Alarm Range Vin2 L1L2 Under | V | Config | uint16 | R/W | 2478 | PIV | Voltage Alarm Range Vin2 L1L2 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2479 | 42480 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L1L2 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L2L3 Under | 2480 | 42481 | Voltage Alarm Range Vin2 L2L3 Under | V | Config | uint16 | R/W | 2480 | PIV | Voltage Alarm Range Vin2 L2L3 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2481 | 42482 | Not Used | [9 empty] | Legacy, Voltage Alarm Range Vin2 L2L3 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Range Vin2 L3L1 Under | 2482 | 42483 | Voltage Alarm Range Vin2 L3L1 Under | V | Config | uint16 | R/W | 2482 | PIV | Voltage Alarm Range Vin2 L3L1 Under | system | 1-660 |  | PS 24 / 48
Not Used | 2483 | 42484 | Not Used | [8 empty] | 1-660 | Legacy, Voltage Alarm Range Vin2 L3L1 Over, unsupported beyond firmware 2.07 | PS 24 / 48
Voltage Alarm Persistence | 2484 | 42485 | Voltage Alarm Persistence | Sec | Config | uint16 | R/W | 2484 | PIV | Voltage Alarm Persistence | system | 15-60 | minimum time is 15 seconds | ALL
Voltage Vin1 Alarm Status Under | 2485 | 42486 | Voltage Vin1 Alarm Status Under |  | Metrology | bitfield8 | R | 2485 | BSV | Voltage Vin1 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | ALL
Not Used | 2486 | 42487 | Not Used | [9 empty] | legacy, Voltage Vin1 Alarm Status Over, unsupported beyond firmware 2.07 | ALL
Voltage Vin2 Alarm Status Under | 2487 | 42488 | Voltage Vin2 Alarm Status Under |  | Metrology | bitfield8 | R | 2487 | BSV | Voltage Vin2 Alarm Status Under | system | 0-63 | Modbus is little-endian (L1-N=bit 0, L2-N=bit 1, L3-N=bit 2, L1-L2=bit 3, L2-L3=bit 4, L3-L1=bit 5) BACnet is big-endian (L1-N=bit 7, L2-N=bit 6, L3-N=bit 5, L1-L2=bit 4, L2-L3=bit 3, L3-L1=bit 2) | PS 24 / 48
Not Used | 2488 | 42489 | Not Used | [9 empty] | Legacy, Voltage Vin2 Alarm Status Over, unsupported beyond firmware 2.07 | PS 24 / 48
Real Time Clock MSW | 2489 | 42490 | Real Time Clock MSW |  | Config | uint16 | R/W | 2489 | PIV | RTC CLOCK | system |  | Number of seconds since Jan 1, 1970 in UTC time | ALL
Real Time Clock LSW | 2490 | 42491 | Real Time Clock LSW |  | Config | uint16 | R/W |  |  |  | system |  |  | ALL
USER CONFIG POINTS 2 | - | - | USER CONFIG POINTS 2 | - | - | - | - | - | - | - | - | - | - | -
System Description 0 | 2601 | 42602 | System Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Name | system | 2 Char |  | ALL
System Description 1 | 2602 | 42603 | System Description 1 | [8 empty] | 2 Char |  | ALL
System Description 2 | 2603 | 42604 | System Description 2 | [8 empty] | 2 Char |  | ALL
System Description 3 | 2604 | 42605 | System Description 3 | [8 empty] | 2 Char |  | ALL
System Description 4 | 2605 | 42606 | System Description 4 | [8 empty] | 2 Char |  | ALL
System Description 5 | 2606 | 42607 | System Description 5 | [8 empty] | 2 Char |  | ALL
System Description 6 | 2607 | 42608 | System Description 6 | [8 empty] | 2 Char |  | ALL
System Description 7 | 2608 | 42609 | System Description 7 | [8 empty] | 2 Char |  | ALL
System Description 8 | 2609 | 42610 | System Description 8 | [8 empty] | 2 Char |  | ALL
System Description 9 | 2610 | 42611 | System Description 9 | [8 empty] | 2 Char |  | ALL
System Description 10 | 2611 | 42612 | System Description 10 | [8 empty] | 2 Char |  | ALL
System Description 11 | 2612 | 42613 | System Description 11 | [8 empty] | 2 Char |  | ALL
System Description 12 | 2613 | 42614 | System Description 12 | [8 empty] | 2 Char |  | ALL
System Description 13 | 2614 | 42615 | System Description 13 | [8 empty] | 2 Char |  | ALL
System Description 14 | 2615 | 42616 | System Description 14 | [8 empty] | 2 Char |  | ALL
System Description 15 | 2616 | 42617 | System Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
Element Description 0 | 2617 | 42618 | Element Description 0 |  | Config | string(32) |  |  | SVO | Property Name Structured View 1-17 | element | 2 Char |  | ALL
Element Description 1 | 2618 | 42619 | Element Description 1 | [8 empty] | 2 Char |  | ALL
Element Description 2 | 2619 | 42620 | Element Description 2 | [8 empty] | 2 Char |  | ALL
Element Description 3 | 2620 | 42621 | Element Description 3 | [8 empty] | 2 Char |  | ALL
Element Description 4 | 2621 | 42622 | Element Description 4 | [8 empty] | 2 Char |  | ALL
Element Description 5 | 2622 | 42623 | Element Description 5 | [8 empty] | 2 Char |  | ALL
Element Description 6 | 2623 | 42624 | Element Description 6 | [8 empty] | 2 Char |  | ALL
Element Description 7 | 2624 | 42625 | Element Description 7 | [8 empty] | 2 Char |  | ALL
Element Description 8 | 2625 | 42626 | Element Description 8 | [8 empty] | 2 Char |  | ALL
Element Description 9 | 2626 | 42627 | Element Description 9 | [8 empty] | 2 Char |  | ALL
Element Description 10 | 2627 | 42628 | Element Description 10 | [8 empty] | 2 Char |  | ALL
Element Description 11 | 2628 | 42629 | Element Description 11 | [8 empty] | 2 Char |  | ALL
Element Description 12 | 2629 | 42630 | Element Description 12 | [8 empty] | 2 Char |  | ALL
Element Description 13 | 2630 | 42631 | Element Description 13 | [8 empty] | 2 Char |  | ALL
Element Description 14 | 2631 | 42632 | Element Description 14 | [8 empty] | 2 Char |  | ALL
Element Description 15 | 2632 | 42633 | Element Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
BACnet Description 0 | 2633 | 42634 | BACnet Description 0 |  | Config | string(32) |  | Dev Obj Prop | DO | Property Description | system | 2 Char |  | ALL
BACnet Description 1 | 2634 | 42635 | BACnet Description 1 | [8 empty] | 2 Char |  | ALL
BACnet Description 2 | 2635 | 42636 | BACnet Description 2 | [8 empty] | 2 Char |  | ALL
BACnet Description 3 | 2636 | 42637 | BACnet Description 3 | [8 empty] | 2 Char |  | ALL
BACnet Description 4 | 2637 | 42638 | BACnet Description 4 | [8 empty] | 2 Char |  | ALL
BACnet Description 5 | 2638 | 42639 | BACnet Description 5 | [8 empty] | 2 Char |  | ALL
BACnet Description 6 | 2639 | 42640 | BACnet Description 6 | [8 empty] | 2 Char |  | ALL
BACnet Description 7 | 2640 | 42641 | BACnet Description 7 | [8 empty] | 2 Char |  | ALL
BACnet Description 8 | 2641 | 42642 | BACnet Description 8 | [8 empty] | 2 Char |  | ALL
BACnet Description 9 | 2642 | 42643 | BACnet Description 9 | [8 empty] | 2 Char |  | ALL
BACnet Description 10 | 2643 | 42644 | BACnet Description 10 | [8 empty] | 2 Char |  | ALL
BACnet Description 11 | 2644 | 42645 | BACnet Description 11 | [8 empty] | 2 Char |  | ALL
BACnet Description 12 | 2645 | 42646 | BACnet Description 12 | [8 empty] | 2 Char |  | ALL
BACnet Description 13 | 2646 | 42647 | BACnet Description 13 | [8 empty] | 2 Char |  | ALL
BACnet Description 14 | 2647 | 42648 | BACnet Description 14 | [8 empty] | 2 Char |  | ALL
BACnet Description 15 | 2648 | 42649 | BACnet Description 15 | [8 empty] | 1 Char NULL | Meter String Block Updated Upon Write to Final Character | ALL
VERIS EMULATION LEGACY REGISTERS | - | - | VERIS EMULATION LEGACY REGISTERS | - | - | - | - | - | - | - | - | - | - | -
Veris Emulation Mode | 2200 | 42201 | Set to Veris Emulation Mode |  | Config | uint16 | R/W |  |  |  | system | 0-1 | 1 = Report Slave ID as Veris Model H8036 | ALL
kWh System LSW | 0 | 40001 | kWh System LSW | kWh | Veris | uint32 | R |  |  |  | element |  |  | ALL
kWh System MSW | 1 | 40002 | kWh System MSW | kWh | Veris |  | R |  |  |  | element |  |  | ALL
kW System | 2 | 40003 | kW System | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVAR System | 3 | 40004 | kVAR System | kVAR | Veris | unit16 | R |  |  |  | element |  |  | ALL
kVA System | 4 | 40005 | kVA System | kVA | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF System | 5 | 40006 | Apparent PF System | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts Line to Line Avg | 6 | 40007 | Volts Line to Line Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts Line to Neutral Avg | 7 | 40008 | Volts Line to Neutral Avg | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps System Avg | 8 | 40009 | Amps System Avg | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L1 | 9 | 40010 | kW L1 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L2 | 10 | 40011 | kW L2 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW L3 | 11 | 40012 | kW L3 | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L1 | 12 | 40013 | Apparent PF L1 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L2 | 13 | 40014 | Apparent PF L2 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Apparent PF L3 | 14 | 40015 | Apparent PF L3 | PF | Veris | unit16 | R |  |  |  | element |  |  | ALL
Volts L1 to L2 | 15 | 40016 | Volts L1 to L2 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to L3 | 16 | 40017 | Volts L2 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to L3 | 17 | 40018 | Volts L1 to L3 | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L1 to Neutral | 18 | 40019 | Volts L1 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L2 to Neutral | 19 | 40020 | Volts L2 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Volts L3 to Neutral | 20 | 40021 | Volts L3 to Neutral | V | Veris | unit16 | R |  |  |  | system |  |  | ALL
Amps L1 | 21 | 40022 | Amps L1 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L2 | 22 | 40023 | Amps L2 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
Amps L3 | 23 | 40024 | Amps L3 | A | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW System Avg | 24 | 40025 | kW System Avg | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Now | 25 | 40026 | kW Demand Sys Now (was Min) | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL
kW Demand Sys Max | 26 | 40027 | kW Demand Sys Max | kW | Veris | unit16 | R |  |  |  | element |  |  | ALL